## revise
[24 empty] | IR test (30sec/1min) |  |  | IR test (1min/10min) |  |  | Ratio DAR
Zone | Subzone | Tripping No | Report No | State | Station | Voltage kV | installation | Date/Time | clean trip source | clean trip point | clean damage area (unfinished) | FailureMode | FailureCause | component | Equip Fails (Cable/Tx/Switchgear/Busbar) | Dispatch Date/Time | Arrival Date/Time | Period (Minute) | Date/Time | Date/Time | Period (Hour) | Date/Time | Period (Hour) | Red | Yellow | Blue | Red2 | Yellow2 | Blue2 | Ratio R | Ratio Y | Ratio B
Northern | K1 | TRIPPING-2020-PLS-1 | 2610/20200111/003 | Perlis | Perlis | 11kV | Underground | 11-01-2020 04:31 | PMU KANGAR CB1 | VCB MAHKAMAH TINGGI KAN00443 | C/SUB PERODUA - BANDARAN | Insulation Failed, Shorted by Old External Damage | Under Investigation | Cable | CABLE | 11-01-2020 04:34 | 11-01-2020 04:59 | 25 | 14-01-2020 15:20, 29-02-2020 01:14 | 29-02-2020 01:04, 29-02-2020 20:54 | 1089, 19 | 29-02-2020 21:20 | 1192.82
Northern | K1 | TRIPPING-2020-KED-24 | 0242/20200112/002 | Kedah | Jitra | 11kV | Underground | 12-01-2020 00:47 | PPU CHANGLOON CL3 | PPU CHANGLOON CL3 | FELDA BT 8 - RUMAH PAM JLN KODIANG | Damaged, Soil Movement | Partly Environment | Cable | CABLE | 12-01-2020 00:50 | 12-01-2020 01:10 | 20 | 12-01-2020 17:44, 13-01-2020 23:56 | 13-01-2020 23:53, 14-01-2020 05:02 | 30, 5 | 14-01-2020 05:20 | 52.55
Northern | K1 | TRIPPING-2020-PLS-2 | 2610/20200113/026 | Perlis | Perlis | 11kV | Underground | 13-01-2020 16:41 | PPU UNIMAP GIS 2K5 | PDB PERLISPLANTATION KJT? CB1 | TPK PELUPUSAN SAMPAH RIMBA MAS - PDB PERLIS DOLOMITE | Damaged, Shorted by Third Party Dug Up | Under Investigation | Cable | CABLE | 13-01-2020 16:55 | 13-01-2020 17:25 | 30 | 14-01-2020 17:51, 14-01-2020 17:54 | 15-01-2020 11:45, 15-01-2020 11:47 | 17, 17 | 15-01-2020 11:54 | 43.22
Northern | K1 | TRIPPING-2020-PLS-3 | 2610/20200113/044 | Perlis | Perlis | 11kV | Underground | 13-01-2020 18:23 | PMU KUALA PERLIS CB12 | PDB KLG SURIME KAN01260 CB1 | PDT KLG TEPONG - PDT KUKUM AUTO MART | Damaged, Shorted by Third Party Dug Up | Improper Laying | Cable | CABLE | 13-01-2020 18:30 | 13-01-2020 19:10 | 40 | 16-01-2020 18:10 | 17-01-2020 09:20 | 15 | 17-01-2020 09:47 | 87.4
Northern | K1 | TRIPPING-2020-PLS-4 | 2610/20200114/003 | Perlis | Perlis | 11kV | Underground | 14-01-2020 05:43 | PMU KANGAR CB2 | PDB TELEKOM LAMA KANGAR KAN01497 CB1 | BILIK SEJUK FAMA - BEHOR TEMAK | Core Opened | Partly Environment | Cable | CABLE | 14-01-2020 05:53 | 14-01-2020 06:40 | 47 | 15-01-2020 23:26 | 09-02-2020 09:10 | 585 | 09-02-2020 09:25 | 627.7
Northern | K1 | TRIPPING-2020-KED-35 | 0245/20200120/010 | Kedah | Kuala Nerang | 11kV | Underground | 20-01-2020 11:00 | PPU KUALA NERANG KN5 | PDB TMN AKASIA KKN00582 CB1 | LDG BKT KETAPANG - LAPS LA2 | Damaged, Shorted by Third Party Dug Up | Unavoidable Accident | Cable | CABLE | 20-01-2020 11:15 | 20-01-2020 11:30 | 15 | 20-01-2020 21:01 | 22-01-2020 18:29 | 45 | 22-01-2020 19:14 | 56.23
Northern | K1 | TRIPPING-2020-KED-40 | 0242/20200121/028 | Kedah | Jitra | 11kV | Underground | 21-01-2020 15:36 | PPU CHANGLOON CL2 | PDB TMN MERBAU KJT01859 CB1 | GENERASI BARU - FELDA LAKA SELATAN | Damaged, Shorted by Third Party Dug Up | Improper Route | Cable | CABLE | 21-01-2020 15:45 | 21-01-2020 16:10 | 25 | 22-01-2020 14:46 | 22-01-2020 19:17 | 4 | 22-01-2020 22:10 | 30.57
Northern | K1 | TRIPPING-2020-PLS-6 | 2610/20200125/023 | Perlis | Perlis | 11kV | Underground | 25-01-2020 23:32 | PMU KUALA PERLIS CB8 | PMU KUALA PERLIS CB8 | KLG PADI ABIDIN ABU BAKAR - KRAF TANGAN | Damaged, Soil Movement | Partly Environment | Cable | CABLE | 25-01-2020 23:37 | 25-01-2020 23:57 | 20 | 26-01-2020 21:47 | 27-01-2020 12:42 | 14 | 27-01-2020 12:53 | 37.35
Northern | K1 | TRIPPING-2020-KED-54 | 0220/20200129/001 | Kedah | Jitra | 11kV | Underground | 29-01-2020 01:02 | PMU TANJUNG PAUH TP14 | PMU TANJUNG PAUH TP14 | TMN MAHSURI FASA 2A - TMN MAHSURI FASA 2C, - PMUTANJUNG PAUH TP14 - PERUMAHAN TANJUNG PAUH FASA 1 | Insulation Failed, Shorted by Old External Damage | Under Investigation | Cable | CABLE | 29-01-2020 01:06 | 29-01-2020 01:29 | 23 | 29-01-2020 10:06, 29-01-2020 12:53, 31-01-2020 15:52 | 29-01-2020 11:53, 22-05-2020 02:37, 31-01-2020 22:42 | 1, 2725, 6 | 22-05-2020 03:25 | 2738.38
Northern | K1 | TRIPPING-2020-PLS-7 | 2610/20200130/029 | Perlis | Perlis | 11kV | Underground | 30-01-2020 22:48 | PMU CHUPING CB3 | PDB UITM ARAU KAN00863 CB1 | S/S B UITM ARAU - PDB KLG BATA | Core Opened | Partly Environment | Cable | CABLE | 30-01-2020 22:49 | 30-01-2020 23:30 | 41 | 14-02-2020 18:21 | 18-04-2020 19:07 | 1536 | 18-04-2020 19:29 | 1892.68
Northern | K1 | TRIPPING-2020-PLS-8 | 2610/20200203/004 | Perlis | Perlis | 11kV | Underground | 03-02-2020 01:29 | PPU SIMPANG EMPAT CB6 | PPU SIMPANG EMPAT CB6 | SEK AGAMA AL ISLAHIAH - SK BOHOR MALI | Core Broken | Defective Manufacture | Cable | CABLE | 03-02-2020 01:30 | 03-02-2020 01:58 | 28 | 05-02-2020 22:42 | 12-03-2020 17:30 | 858 | 12-03-2020 18:17 | 928.8
Northern | K1 | TRIPPING-2020-KED-73 | 0245/20200205/001 | Kedah | Kuala Nerang | 11kV | Underground | 05-02-2020 08:26 | PPU KUALA NERANG KN2 | PPU KUALA NERANG KN2 | PADAT LADANG AYAM KG BAROKHAS | Insulation Failed and Shorted by Animal | Partly Environment | Cable Termination | SWITCHGEAR | 05-02-2020 08:30 | 05-02-2020 09:00 | 30 | 05-02-2020 19:08 | 05-02-2020 20:54 | 1 | 05-02-2020 21:30 | 13.07
Northern | K1 | TRIPPING-2020-KED-82 | 0242/20200210/056 | Kedah | Jitra | 11kV | Underground | 10-02-2020 22:07 | PPU KODIANG KD1 | JIN TEIK ORGANIK KJT01187 |  | Insulation Failed, Shorted by Water Ingress | Partly Environment | Cable | OTHER | 10-02-2020 22:32 | 10-02-2020 22:50 | 18 |  |  |  | 10-02-2020 23:30 | 1.38
Northern | K1 | TRIPPING-2020-PLS-11 | 2610/20200222/050 | Perlis | Perlis | 11kV | Underground | 22-02-2020 13:42 | PMU KANGAR CB12 | PMU KANGAR CB12 | PDT PEJ KEDAI JLN SYED ALWI - TELEKOM LAMA | Damaged, Shorted by Third Party Dug Up | Improper Laying | Cable | CABLE | 22-02-2020 13:45 | 22-02-2020 14:02 | 17 | 06-03-2020 23:03 | 07-03-2020 12:02 | 12 | 07-03-2020 12:10 | 334.47
Northern | K1 | TRIPPING-2020-KED-108 | 2810/20200223/005 | Kedah | Jitra | 11kV | Underground | 23-02-2020 11:02 | PPU DARULAMAN 1K5 | TMN NILAM KENCHANA KJT19364 CB1 | PDB TMN SINAR HARAPAN - MRSM JITRA | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 23-02-2020 11:25 | 23-02-2020 11:30 | 5 | 23-02-2020 23:10 | 24-02-2020 21:40 | 22 | 24-02-2020 22:10 | 35.13
Northern | K1 | TRIPPING-2020-PLS-12 | 2610/20200225/019 | Perlis | Perlis | 11kV | Underground | 25-02-2020 17:14 | PPU BUKIT KETERI 7K5 | PPU BUKIT KETERI 7K5 | SM BESERI - SEMADONG 1 | Core Opened | Partly Environment | Cable | CABLE | 25-02-2020 17:34 | 25-02-2020 18:18 | 44 | 05-03-2020 12:37, 06-03-2020 02:51 | 06-03-2020 07:16, 06-03-2020 07:17 | 18, 4 | 06-03-2020 03:50 | 226.6
Northern | K1 | TRIPPING-2020-PLS-13 | 2610/20200302/022 | Perlis | Perlis | 11kV | Underground | 02-03-2020 19:50 | PPU UNIMAP GIS 2K5 | PDB BATU BERTANGKUP KAN00097 CB1 | PBT BILAL UDOH - PBT KUBANG TIGA | Core Opened | Partly Environment | Cable | CABLE | 02-03-2020 19:55 | 02-03-2020 20:20 | 25 | 07-03-2020 21:23, 18-03-2020 21:34 | 18-03-2020 21:33, 19-03-2020 13:06 | 264, 15 | 19-03-2020 13:16 | 401.43
Northern | K1 | TRIPPING-2020-PLS-14 | 2610/20200303/013 | Perlis | Perlis | 11kV | Underground | 03-03-2020 10:52 | PPU UNIMAP GIS 2K5 | PDB PERLISPLANTATION KAN00236 CB1 | PLB KUARI BATU REPUT - CVIA CENTRE | Failed, Shorted by Old External Damage | Partly Environment | Straight Through Joint | CABLE | 03-03-2020 10:52 | 03-03-2020 11:37 | 45 | 03-03-2020 17:38, 03-03-2020 23:22 | 03-03-2020 20:57, 04-03-2020 12:39 | 3, 13 | 04-03-2020 12:48 | 25.93
Northern | K1 | TRIPPING-2020-PLS-15 | 2610/20200308/009 | Perlis | Perlis | 11kV | Underground | 08-03-2020 09:48 | PPU POLITEKNIK PAUH PERLIS 2 | PPU POLITEKNIK PAUH PERLIS CB2 | TMN KURUNG INAI - FELCRA LAKA SELATAN | Damaged, Shorted by Third Party Dug Up | Improper Laying | Cable | CABLE | 08-03-2020 09:55 | 08-03-2020 10:25 | 30 | 10-03-2020 14:58 | 11-03-2020 08:57 | 17 | 11-03-2020 09:06 | 71.3
Northern | K1 | TRIPPING-2020-KED-129 | 0242/20200308/014 | Kedah | Jitra | 11kV | Underground | 08-03-2020 10:22 | PMU BUKIT KAYU HITAM BKH8 | STN SUIS ICQS KJT19258 CB1 | ICQS | Insulation Burnt | Partly Environment | Cable Termination | SWITCHGEAR | 08-03-2020 11:17 | 08-03-2020 12:07 | 50 | 09-03-2020 15:50, 09-03-2020 19:03 | 09-03-2020 23:36, 09-03-2020 23:35 | 7, 4 | 10-03-2020 00:55 | 38.55
Northern | K1 | TRIPPING-2020-KED-134 | 0242/20200310/009 | Kedah | Jitra | 11kV | Underground | 10-03-2020 12:17 | PPU CHANGLOON CL2 | PDB TMN MERBAU KJT01859 CB1 | GENERASI BARU FELDA LAKA SELATAN - FELDA LAKA SELATAN | Failed, Shorted by Corrosive Evmnt | Under Investigation | Straight Through Joint | CABLE | 10-03-2020 12:21 | 10-03-2020 12:50 | 29 | 10-03-2020 16:28 | 10-03-2020 18:30 | 2 | 10-03-2020 19:30 | 7.22
Northern | K1 | TRIPPING-2020-KED-139 | 0242/20200312/010 | Kedah | Jitra | 11kV | Underground | 12-03-2020 12:30 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01797 CB1 |  | Terminal Shorted by Animal / Insects | Partly Environment | Cable Termination | TRANSIENT | 12-03-2020 12:50 | 12-03-2020 13:20 | 30 |  |  |  | 12-03-2020 13:50 | 1.33
Northern | K1 | TRIPPING-2020-KED-142 | 0242/20200314/001 | Kedah | Jitra | 11kV | Underground | 14-03-2020 03:50 | PMU BUKIT KAYU HITAM BKH6 | PMU BUKIT KAYU HITAM BKH6 | PMUBUKIT KAYU HITAM BKH6 - SSD KLG ACM | Damaged, Shorted by Third Party Dug Up | Improper Laying | Cable | CABLE | 14-03-2020 03:53 | 14-03-2020 04:21 | 28 | 14-03-2020 15:02 | 15-03-2020 05:00 | 13 | 15-03-2020 06:15 | 26.42
Northern | K1 | TRIPPING-2020-KED-143 | 0242/20200314/002 | Kedah | Jitra | 11kV | Underground | 14-03-2020 03:52 | PMU BUKIT KAYU HITAM BKH7 | PMU BUKIT KAYU HITAM BKH7 | PDB KMC STORAGE - SSD KLG ACM | Damaged, Shorted by Third Party Dug Up | Improper Laying | Cable | CABLE | 14-03-2020 03:53 | 14-03-2020 04:21 | 28 |  |  |  | 15-03-2020 06:15 | 26.38
Northern | K1 | TRIPPING-2020-KED-164 | 0245/20200319/009 | Kedah | Kuala Nerang | 11kV | Underground | 19-03-2020 03:22 | PPU KUALA NERANG KN3 | PPU KUALA NERANG KN3 | PBT KG. PERIK - PAT KG. BAYAS-ALS | Failed, Shorted by Corrosive Evmnt | Partly Environment | Straight Through Joint | CABLE | 19-03-2020 03:25 | 19-03-2020 03:26 | 1 | 19-03-2020 20:28 | 26-03-2020 20:00 | 167 | 26-03-2020 21:04 | 185.7
Northern | K1 | TRIPPING-2020-PLS-16 | 2610/20200322/009 | Perlis | Perlis | 11kV | Underground | 22-03-2020 13:27 | PMU KUALA PERLIS CB6 | SK PANGGAU KAN00425 CB1 | SAT PPRT TOK KUNING - PPRT TOK KUNING | Failed, Shorted by Old External Damage | Under Investigation | Straight Through Joint | CABLE | 22-03-2020 13:33 | 22-03-2020 14:03 | 30 | 22-03-2020 18:05 | 24-03-2020 00:44 | 30 | 24-03-2020 00:40 | 35.22
Northern | K1 | TRIPPING-2020-PLS-17 | 2610/20200323/046 | Perlis | Perlis | 11kV | Underground | 23-03-2020 09:00 | PMU KANGAR CB3 | PDB KOMP KASTAM KANGAR KAN00494 CB1 | PAT KG PETAI | Dielectric breakdown | Dielectric Deterioration | Cable Termination | SWITCHGEAR | 23-03-2020 09:17 |  | 0 |  |  |  | 23-03-2020 16:25 | 7.42
Northern | K1 | TRIPPING-2020-PLS-18 | 2610/20200328/009 | Perlis | Perlis | 11kV | Underground | 28-03-2020 02:11 | PMU CHUPING CB4 | PDB TMN DESA PAUH KAN00925 CB1 | TAPAK PELUPUSAN SPH PDG SIDING - PBT PADANG SIDING | Core Opened | Partly Environment | Cable | CABLE | 28-03-2020 02:32 | 28-03-2020 02:55 | 23 | 28-03-2020 21:33 | 29-03-2020 21:35 | 24 | 29-03-2020 21:55 | 43.73
Northern | K1 | TRIPPING-2020-KED-183 | 0242/20200329/033 | Kedah | Jitra | 11kV | Underground | 29-03-2020 08:31 | PPU UUM SINTOK ST6 | PDB ASRAMA UUM KJT01743 CB1 | SS BUKIT DIMAN - SSD RUMAH PAM GENTING IBAI | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 29-03-2020 08:39 | 29-03-2020 09:23 | 44 | 29-03-2020 12:45 | 30-03-2020 11:16 | 22 | 30-03-2020 11:46 | 27.25
Northern | K1 | TRIPPING-2020-KED-195 | 0242/20200401/029 | Kedah | Jitra | 11kV | Underground | 01-04-2020 07:27 | PPU KODIANG KD2 | SM TG BENDAHARA KJT01260 | KG TOK ARANG 1 - KG PERING | Core Opened | Defective Manufacture | Cable | CABLE | 01-04-2020 07:37 | 01-04-2020 07:40 | 3 | 03-04-2020 12:00 | 03-04-2020 19:01 | 7 | 03-04-2020 19:15 | 59.8
Northern | K1 | TRIPPING-2020-PLS-20 | 2610/20200409/001 | Perlis | Perlis | 11kV | Underground | 09-04-2020 00:25 | PPU PADANG BESAR CB9 | PDB TITI TINGGI KAN00091 CB1 |  |  |  |  | TRANSIENT | 09-04-2020 00:35 | 09-04-2020 00:40 | 5 |  |  |  | 09-04-2020 02:23 | 1.97
Northern | K1 | TRIPPING-2020-PLS-21 | 2610/20200410/019 | Perlis | Perlis | 11kV | Underground | 10-04-2020 14:46 | PPU SHORUBBER CB5 | BEHOR MENTALOON KAN00974 CB1 | PLB BEHOR MENTALOON - PAT SEMUT GATAL | Failed, Shorted by Corrosive Evmnt | Partly Environment | Straight Through Joint | CABLE | 10-04-2020 14:55 | 10-04-2020 15:31 | 36 | 11-04-2020 10:31, 15-04-2020 11:00, 15-04-2020 13:35 | 15-04-2020 02:52, 15-04-2020 11:44, 15-04-2020 15:16 | 88, 0, 1 | 15-04-2020 13:12 | 118.43
Northern | K1 | TRIPPING-2020-PLS-22 | 2610/20200410/052 | Perlis | Perlis | 11kV | Underground | 10-04-2020 18:36 | PPU SHORUBBER CB2 | PDB ALOR LANCANG KAN00834 CB1 | ALOR LANCANG - PAT ALOR ARA TIMUR | Failed, Shorted by Corrosive Evmnt | Under Investigation | Straight Through Joint | CABLE | 10-04-2020 18:39 | 10-04-2020 19:04 | 25 | 11-04-2020 10:35 | 11-05-2020 16:20 | 725 | 11-05-2020 16:33 | 741.95
Northern | K1 | TRIPPING-2020-KED-220 | 0242/20200411/002 | Kedah | Jitra | 11kV | Substation | 11-04-2020 06:55 | PPU DARULAMAN 4K5 | KG KETUL - KETUL KJT00102 |  | Terminal Shorted by Animal / Insects | Partly Environment | Drop Out Fuse | TRANSIENT | 11-04-2020 07:06 | 11-04-2020 08:00 | 54 |  |  |  | 11-04-2020 08:31 | 1.6
Northern | K1 | TRIPPING-2020-PLS-23 | 2610/20200414/004 | Perlis | Perlis | 11kV | Underground | 14-04-2020 04:45 | PPU SHORUBBER CB8 | PDB SMPG ABI KAN00315 CB1 |  |  |  |  | TRANSIENT | 14-04-2020 04:47 | 14-04-2020 05:14 | 27 |  |  |  | 14-04-2020 05:38 | 0.88
Northern | K1 | TRIPPING-2020-PLS-24 | 2610/20200414/050 | Perlis | Perlis | 11kV | Underground | 14-04-2020 11:28 | PPU PADANG BESAR CB9 | PDB PEKAN KAKI BUKIT KAN00140 | PEKAN KAKI BUKIT - PDB RPA WANG KELIAN | Dropped | Partly Environment | ABC Conductor | OVERHEAD LINES | 14-04-2020 11:35 | 14-04-2020 12:18 | 43 | 14-04-2020 18:35 | 15-04-2020 23:38 | 29 | 16-04-2020 00:10 | 36.7
Northern | K1 | TRIPPING-2020-PLS-25 | 2610/20200414/120 | Perlis | Perlis | 11kV | Underground | 14-04-2020 18:26 | PMU CHUPING CB7 | TMN SRI PUTERI KAN00810 | ALOR ARA - TMN DESA NYU | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 14-04-2020 18:46 | 14-04-2020 19:10 | 24 | 14-04-2020 22:06 | 15-04-2020 12:38 | 14 | 15-04-2020 12:53 | 18.45
Northern | K1 | TRIPPING-2020-PLS-26 | RE/2610/20200415/PLS/26 | Perlis | Perlis | 11kV | Underground | 15-04-2020 15:49 | PMU CHUPING CB7 | SK GUAR NANGKA KAN02604 |  |  |  |  | OTHER | 15-04-2020 15:54 |  | 0 |  |  |  | 16-04-2020 21:57 | 30.13
Northern | K1 | TRIPPING-2020-KED-234 | 0242/20200416/004 | Kedah | Jitra | 11kV | Underground | 16-04-2020 11:58 | PPU KODIANG KD5 | PPU KODIANG KD5 | PPUKODIANG KD5 - PDB RUMAH PAM SG. PERING | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 16-04-2020 12:05 | 16-04-2020 12:35 | 30 | 16-04-2020 15:18, 17-04-2020 16:04 | 19-04-2020 18:16, 17-04-2020 19:33 | 74, 3 | 19-04-2020 18:50 | 78.87
Northern | K1 | TRIPPING-2020-PLS-27 | 2610/20200418/002 | Perlis | Perlis | 11kV | Substation | 18-04-2020 03:21 | PPU PADANG BESAR CB9 | SIMPANG JALAN SAHABAT KAN02267 |  | Terminal Shorted by Animal / Insects | Partly Environment | Drop Out Fuse | TRANSIENT | 18-04-2020 04:35 | 18-04-2020 04:38 | 3 |  |  |  | 18-04-2020 05:17 | 1.93
Northern | K1 | TRIPPING-2020-PLS-28 | 0242/20200418//005 | Kedah | Jitra | 11kV | Underground | 18-04-2020 10:25 | PPU LOJI AIR ARAU GIS 11K5 | PDB KLG BERAS PERING KJT01775 |  | Broken | Partly Environment | Lightning Arrester | OTHER | 18-04-2020 10:28 | 18-04-2020 11:12 | 44 |  |  |  | 18-04-2020 12:00 | 1.58
Northern | K1 | TRIPPING-2020-PLS-29 | 2610/20200420/021 | Perlis | Perlis | 11kV | Substation | 20-04-2020 20:22 | PPU LOJI AIR ARAU GIS 5K5 | PPU LOJI AIR ARAU GIS 5K5 | PAT MADA GUAR SANJI - PDB RUMAH PAM GUAR SANJI | Broken | Partly Environment | Lightning Arrester | SWITCHGEAR | 20-04-2020 20:28 | 20-04-2020 20:58 | 30 | 21-04-2020 10:42 | 21-04-2020 12:10 | 1 | 22-04-2020 13:10 | 40.8
Northern | K1 | TRIPPING-2020-PLS-30 | 2610/20200421/060 | Perlis | Perlis | 11kV | Underground | 21-04-2020 17:36 | PMU KUALA PERLIS CB5 | PMU KUALA PERLIS CB5 | PLB LOT 764 TMN KUALA PERLIS - KLG AIS IGLOO | Core Opened | Defective Manufacture | Cable | CABLE | 21-04-2020 17:38 |  | 0 | 22-04-2020 09:49 | 23-04-2020 12:27 | 26 | 23-04-2020 12:37 | 43.02
Northern | K1 | TRIPPING-2020-KED-251 | 0242/20200422/008 | Kedah | Jitra | 11kV | Underground | 22-04-2020 08:02 | PPU UUM SINTOK ST6 | ASRAMA UUM KJT01743 |  | Dielectric breakdown | Dielectric Deterioration | Cable Termination | OTHER | 22-04-2020 08:04 | 22-04-2020 08:52 | 48 |  |  |  | 22-04-2020 09:55 | 1.88
Northern | K1 | TRIPPING-2020-KED-261 | 0245/20200424/007 | Kedah | Kuala Nerang | 11kV | Underground | 24-04-2020 15:06 | PPU NAKA 6K5 | PPU NAKA 6K5 | PBT KG. PADANG - PBT SG. KAP2 | Core Opened | Under Investigation | Cable | CABLE | 24-04-2020 15:20 | 24-04-2020 15:35 | 15 | 24-04-2020 22:12 | 25-04-2020 22:04 | 23 | 25-04-2020 23:04 | 31.97
Northern | K1 | TRIPPING-2020-PLS-31 | 2610/20200426/002 | Perlis | Perlis | 11kV | Underground | 26-04-2020 06:00 | PPU SIMPANG EMPAT CB1 | KLG PADI MAJU KAN01038 |  | Terminal Shorted by Animal / Insects | Partly Environment | Drop Out Fuse | TRANSIENT | 26-04-2020 06:04 | 26-04-2020 06:31 | 27 |  |  |  | 26-04-2020 07:40 | 1.67
Northern | K1 | TRIPPING-2020-PLS-32 | 2610/20200428/003 | Perlis | Perlis | 11kV | Underground | 28-04-2020 04:11 | PPU BUKIT KETERI 5K5 | RPA CHUPING NO 2 KAN00285 | RPA CHUPING NO 2 - TMN EMAS | Core Opened | Defective Manufacture | Cable | CABLE | 28-04-2020 04:35 | 28-04-2020 05:00 | 25 | 07-05-2020 09:17 | 08-05-2020 04:17 | 19 | 08-05-2020 04:34 | 240.38
Northern | K1 | TRIPPING-2020-PLS-33 | 2610/20200503/018 | Perlis | Perlis | 11kV | Underground | 03-05-2020 16:38 | PPU UNIMAP GIS 2K5 | BATU BERTANGKUP KAN00098 | BILAL UDOH - KUBANG TIGA | Core Opened | Defective Manufacture | Cable | CABLE | 03-05-2020 16:45 | 03-05-2020 17:11 | 26 | 04-05-2020 11:30 | 11-05-2020 15:07 | 171 | 11-05-2020 15:45 | 191.12
Northern | K1 | TRIPPING-2020-PLS-34 | 2610/20200505/001 | Perlis | Perlis | 11kV | Underground | 05-05-2020 02:56 | PPU PADANG BESAR CB9 | PDB TITI TINGGI KAN00091 CB1 | PBT BUKIT CABANG - PLB TITI TINGGI ULU | Core Broken | Defective Manufacture | Cable | CABLE | 05-05-2020 02:59 | 05-05-2020 03:25 | 26 | 13-05-2020 16:50 | 21-05-2020 11:22 | 186 | 21-05-2020 11:58 | 393.03
Northern | K1 | TRIPPING-2020-KED-288 | 0242/20200508/062 | Kedah | Jitra | 11kV | Overhead | 08-05-2020 20:14 | PMU KANGAR 1L5 | KANGAR 1K5 A/R JUMPER | A/R KANGAR 1L4 | Jumper Snapped | Lightning | Auto Recloser | OVERHEAD LINES | 08-05-2020 20:24 | 08-05-2020 20:51 | 27 | 08-05-2020 23:22 | 09-05-2020 04:28 | 5 | 09-05-2020 05:14 | 9
Northern | K1 | TRIPPING-2020-KED-293 | 0242/20200509/046 | Kedah | Jitra | 11kV | Overhead | 09-05-2020 21:30 | PPU JERLUN SJ2 | KLG PROSES UDANG KERPAN KJT01687 | 3S SS SAMAK - KUALA TUNJANG, - KUALA TUNJANG - PEKAN AIR HITAM | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 09-05-2020 21:33 | 09-05-2020 22:10 | 37 | 10-05-2020 23:01, 10-05-2020 23:03 | 11-05-2020 16:24, 14-05-2020 12:37 | 17, 85 | 14-05-2020 13:50 | 112.33
Northern | K1 | TRIPPING-2020-PLS-35 | 2610/20200511/005 | Perlis | Perlis | 11kV | Underground | 11-05-2020 04:32 | PPU SIMPANG EMPAT CB4 | PPU SIMPANG EMPAT CB4 |  | Opened and Shorted by Animal | Partly Environment | HV Cable (Tx Tail) | TRANSIENT | 11-05-2020 04:38 | 11-05-2020 05:17 | 39 |  |  |  | 11-05-2020 06:08 | 1.6
Northern | K1 | TRIPPING-2020-KED-306 | 0242/20200515/010 | Kedah | Jitra | 11kV | Underground | 15-05-2020 11:33 | PPU UUM SINTOK ST3 | PPU UUM SINTOK ST3 | PUSAT PEMBANGUNAN EKS UUM - PDB RMH PAM RISDA TG GENTING | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 15-05-2020 11:40 | 15-05-2020 12:16 | 36 | 15-05-2020 22:51 | 16-05-2020 01:36 | 2 | 16-05-2020 01:44 | 14.18
Northern | K1 | TRIPPING-2020-PLS-37 | 2610/20200519/030 | Perlis | Perlis | 11kV | Underground | 19-05-2020 19:23 | PPU POLITEKNIK PAUH PERLIS 2 | PPU POLITEKNIK PAUH PERLIS CB2 | L/S FELCRA ULU PAUH - TMN INDUSTRI PAUH | Dielectric | Dielectric Deterioration | RMU SF6 | CABLE | 19-05-2020 19:24 | 19-05-2020 20:00 | 36 | 20-05-2020 21:33, 21-05-2020 01:16, 22-05-2020 10:17 | 21-05-2020 00:59, 22-05-2020 17:26, 22-05-2020 17:31 | 3, 40, 7 | 22-05-2020 18:28 | 71.08
Northern | K1 | TRIPPING-2020-KED-337 | 0245/20200527/011 | Kedah | Kuala Nerang | 11kV | Underground | 27-05-2020 14:19 | PPU KUALA NERANG KN1 | PPU KUALA NERANG KN1 | PBT KUBANG KENDONG 2 - PLB TANJUNG SEBERANG | Dielectric breakdown | Improper Installation | Cable Termination | CABLE | 27-05-2020 14:23 | 27-05-2020 14:31 | 8 | 27-05-2020 20:37 | 28-05-2020 02:18 | 5 | 28-05-2020 03:10 | 12.85
Northern | K1 | TRIPPING-2020-KED-346 | 0242/20200601/025 | Kedah | Jitra | 11kV | Underground | 01-06-2020 13:01 | PPU DARULAMAN 1K5 | PPU DARULAMAN 1K5 | EMERALD SAUJANA - PDB TMN MUTIARA INDAH | Insulation Failed, Shorted by Corrosive Evmnt | Partly Environment | Cable | CABLE | 01-06-2020 13:03 | 01-06-2020 13:20 | 17 | 03-06-2020 14:08 | 06-06-2020 06:03 | 63 | 06-06-2020 12:20 | 119.32
Northern | K1 | TRIPPING-2020-KED-359 | 0242/20200606/032 | Kedah | Jitra | 11kV | Underground | 06-06-2020 19:23 | PPU CHANGLOON CL3 | PPU CHANGLOON CL3 | PAT RUMAH PAM JALAN KODIANG - PLD FELDA BATU 8 CHANGLUN | Failed, Shorted by Corrosive Evmnt | Partly Environment | Straight Through Joint | CABLE | 06-06-2020 19:25 | 06-06-2020 19:55 | 30 | 07-06-2020 12:40 | 10-06-2020 06:05 | 65 | 10-06-2020 07:10 | 83.78
Northern | K1 | TRIPPING-2020-PLS-38 | 2610/20200612/003 | Perlis | Perlis | 11kV | Underground | 12-06-2020 07:53 | PMU KANGAR CB1 | PDB SEKOLAH VOKASIONAL KANGAR KAN00475 CB1 | PDB TELEKOM BARU KANGAR - STADIUM UTAMA KANGAR | Core Opened | Partly Environment | Cable | CABLE | 12-06-2020 07:55 | 12-06-2020 08:30 | 35 | 13-06-2020 22:47 | 21-06-2020 16:13 | 185 | 21-06-2020 16:39 | 224.77
Northern | K1 | TRIPPING-2020-KED-369 | 0245/20200613/005 | Kedah | Kuala Nerang | 11kV | Underground | 13-06-2020 17:02 | PPU KUALA NERANG KN4 | PPU KUALA NERANG KN4 | PDB PEKAN BARU KNG - PDB PEKAN KUALA NERANG | Failed, Shorted by Old External Damage | Partly Environment | Straight Through Joint | CABLE | 13-06-2020 17:02 | 13-06-2020 17:13 | 11 | 13-06-2020 20:23 | 16-06-2020 00:43 | 52 | 16-06-2020 10:10 | 65.13
Northern | K1 | TRIPPING-2020-KED-370 | 0242/20200613/021 | Kedah | Jitra | 11kV | Underground | 13-06-2020 21:59 | PPU CHANGLOON CL1 | PPU CHANGLOON CL1 | HOSBA - PEKAN ASUN | Core Opened | Partly Environment | Cable | CABLE | 13-06-2020 22:01 | 13-06-2020 22:23 | 22 | 14-06-2020 10:20 | 15-06-2020 21:04 | 34 | 15-06-2020 21:30 | 47.52
Northern | K1 | TRIPPING-2020-PLS-39 | 0242/20200615/013 | Perlis | Perlis | 11kV | Underground | 15-06-2020 13:13 | PPU LOJI AIR ARAU GIS 11K5 | PDB KLG BERAS PERING KJT01775 CB1 | PIDA 12B | Core Opened | Partly Environment | Cable | OVERHEAD LINES | 15-06-2020 13:14 | 15-06-2020 13:44 | 30 |  |  |  | 15-06-2020 15:31 | 2.3
Northern | K1 | TRIPPING-2020-KED-375 | 0242/20200615/029 | Kedah | Jitra | 11kV | Underground | 15-06-2020 17:16 | PMU TANJUNG PAUH TP15 | PMU TANJUNG PAUH TP15 | PMUTANJUNG PAUH TP15 - PDB KAWAN SUPERMARKET | Core Opened | Partly Environment | Cable | CABLE | 15-06-2020 17:22 | 15-06-2020 17:40 | 18 | 16-06-2020 14:36 | 25-06-2020 06:21 | 207 | 25-06-2020 07:15 | 229.98
Northern | K1 | TRIPPING-2020-KED-377 | 0245/20200616/001 | Kedah | Kuala Nerang | 11kV | Underground | 16-06-2020 00:52 | PPU NAKA 3K5 | PBT KUBANG BEMBAN KKN00177 CB1 | KUBANG BEMBAN - PATOD KUBANG BEMBAN DALAM | Core Opened | Partly Environment | Cable | CABLE | 16-06-2020 02:00 | 16-06-2020 02:28 | 28 |  |  |  | 17-06-2020 11:15 | 34.38
Northern | K1 | TRIPPING-2020-KED-381 | 0242/20200619/006 | Kedah | Jitra | 11kV | Underground | 19-06-2020 11:35 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00895 | PATOD HOSBA - PLB PEKAN ASUN | Core Opened | Partly Environment | Cable | CABLE | 19-06-2020 11:42 | 19-06-2020 12:10 | 28 | 20-06-2020 16:07 | 21-06-2020 00:03 | 7 | 21-06-2020 21:31 | 57.93
Northern | K1 | TRIPPING-2020-KED-385 | 0242/20200621/090 | Kedah | Jitra | 11kV | Underground | 21-06-2020 19:47 | PPU DARULAMAN 6K5 | PPU DARULAMAN 6K5 | PDB RUMAH PAM JPS GELONG - PDB HOSPITAL JITRA | Core Opened | Defective Manufacture | Cable | CABLE | 21-06-2020 19:49 | 21-06-2020 20:10 | 21 | 22-06-2020 00:00 | 08-07-2020 04:13 | 388 | 18-07-2020 18:29 | 646.7
Northern | K1 | TRIPPING-2020-PLS-40 | 2610/20200623/001 | Perlis | Perlis | 11kV | Overhead | 23-06-2020 02:20 | PMU KUALA PERLIS CB2 | PMU KUALA PERLIS CB2 | PMUKUALA PERLIS CB2 - TMN BUNGA PADI | Failed, Shorted by Old External Damage | Partly Environment | Straight Through Joint | OVERHEAD LINES | 23-06-2020 02:32 | 23-06-2020 02:49 | 17 | 25-06-2020 16:24 | 01-07-2020 09:49 | 137 | 01-07-2020 12:08 | 201.8
Northern | K1 | TRIPPING-2020-PLS-41 | 2610/20200623/070 | Perlis | Perlis | 11kV | Underground | 23-06-2020 15:47 | PMU KANGAR CB1 | PDB SEKOLAH VOKASIONAL KANGAR KAN00472 CB1 | PDB SEKOLAH VOKASIONAL KANGAR - PDB SK SRI INDRA | Core Opened | Partly Environment | Cable | CABLE | 23-06-2020 15:48 | 23-06-2020 15:55 | 7 |  |  |  | 06-07-2020 10:56 | 307.15
Northern | K1 | TRIPPING-2020-KED-409 | 0245/20200701/011 | Kedah | Kuala Nerang | 11kV | Underground | 01-07-2020 15:19 | PPU NAKA 6K5 | PPU NAKA 6K5 | PBT KG. BAGAN - PBT KG. CHANDING | Core Opened | Partly Environment | Cable | CABLE | 01-07-2020 15:20 | 01-07-2020 15:50 | 30 | 01-07-2020 18:20 | 02-07-2020 16:21 | 22 | 02-07-2020 17:40 | 26.35
Northern | K1 | TRIPPING-2020-KED-411 | 0242/20200703/004 | Kedah | Jitra | 11kV | Underground | 03-07-2020 05:53 | PPU DARULAMAN 10K5 | PPU DARULAMAN 10K5 | PAT CHIP SENG HENG - PDB TMN RASA SAYANG | Core Opened | Defective Manufacture | Cable | CABLE | 03-07-2020 06:05 | 03-07-2020 06:46 | 41 | 03-07-2020 22:45 | 04-07-2020 04:52 | 6 | 05-07-2020 17:20 | 59.45
Northern | K1 | TRIPPING-2020-KED-413 | 0242/20200704/007 | Kedah | Jitra | 11kV | Underground | 04-07-2020 13:59 | PPU JERLUN SJ6 | PPU JERLUN SJ6 | PPUJERLUN SJ6 - PAT AIR HITAM | Core Opened | Partly Environment | Cable | CABLE | 04-07-2020 14:17 | 04-07-2020 14:45 | 28 | 04-07-2020 21:29 | 05-07-2020 08:08 | 10 | 05-07-2020 13:14 | 23.25
Northern | K1 | TRIPPING-2020-KED-414 | 0242/20200704/039 | Kedah | Jitra | 11kV | Underground | 04-07-2020 15:11 | PPU DARULAMAN 8K5 | PPU DARULAMAN 8K5 | PBT DRIVING RANGE - TMN GOLF 4, - PBT DRIVING RANGE - PDB PLAZA TOL JITRA | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 04-07-2020 15:16 | 04-07-2020 15:30 | 14 | 05-07-2020 16:20, 05-07-2020 21:59 | 05-07-2020 18:23, 06-07-2020 04:09 | 2, 6 | 06-07-2020 04:12 | 37.02
Northern | K1 | TRIPPING-2020-PLS-42 | 2610/20200705/003 | Perlis | Perlis | 11kV | Underground | 05-07-2020 07:52 | PPU SHORUBBER CB2 | PDB ALOR LANCANG KAN00833 CB1 | PDT KUKUM KUBANG GAJAH - PDB SK KUBANG GAJAH | Core Opened | Partly Environment | Cable | CABLE | 05-07-2020 07:54 | 05-07-2020 08:25 | 31 | 06-07-2020 22:26 | 17-08-2020 08:50 | 994 | 17-08-2020 09:00 | 1033.13
Northern | K1 | TRIPPING-2020-PLS-44 | 2610/20200707/026 | Perlis | Perlis | 11kV | Underground | 07-07-2020 16:55 | PPU POLITEKNIK PAUH PERLIS | POLITEKNIK PAUH PERLIS CB2 | MRSM ULU PAUH - TMN KURUNG INAI | Core Opened | Partly Environment | Cable | CABLE | 07-07-2020 16:57 | 07-07-2020 17:24 | 27 | 08-07-2020 23:19 | 02-09-2020 08:58 | 1329 | 02-09-2020 09:17 | 1360.37
Northern | K1 | TRIPPING-2020-PLS-45 | 2610/20200710/003 | Perlis | Perlis | 11kV | Underground | 10-07-2020 07:11 | PPU MINI PPU ABI 1K5 | PPU MINI PPU ABI 1K5 | PLB KUARI BATU TEONG CHAI - PVCB SIMPANG ABI | Insulation Failed, Shorted by Corrosive Evmnt | Partly Environment | Cable | CABLE | 10-07-2020 07:30 | 10-07-2020 08:01 | 31 | 12-07-2020 22:28 | 05-08-2020 20:41 | 574 | 10-08-2020 18:00 | 754.82
Northern | K1 | TRIPPING-2020-KED-433 | 0242/20200716/001 | Kedah | Jitra | 11kV | Underground | 16-07-2020 08:22 | PPU KODIANG KD1 | PDB JIN TEIK ORGANIK KJT01187 CB1 | PAT CEROK MOKAM 1 | Insulation Burnt | Partly Environment | Cable Termination | CABLE | 16-07-2020 08:40 | 16-07-2020 09:10 | 30 | 16-07-2020 14:14 | 16-07-2020 20:56 | 6 | 16-07-2020 22:25 | 14.05
Northern | K1 | TRIPPING-2020-KED-434 | 0242/20200717/001 | Kedah | Jitra | 11kV | Underground | 17-07-2020 03:32 | PPU DARULAMAN 6K5 | PPU DARULAMAN 6K5 |  | Core Opened | Defective Manufacture | Cable | TRANSIENT | 17-07-2020 03:39 | 17-07-2020 03:49 | 10 |  |  |  | 17-07-2020 04:05 | 0.55
Northern | K1 | TRIPPING-2020-KED-445 | 0242/20200725/041 | Kedah | Jitra | 11kV | Underground | 25-07-2020 10:56 | PPU DARULAMAN 10K5 | PPU DARULAMAN 10K5 | MUTIARA RESIDENT NO 2 - STN SUIS 11KV IKBN JITRA | Damaged, Soil Movement | Partly Environment | Cable | CABLE | 25-07-2020 10:57 | 25-07-2020 11:28 | 31 |  |  |  | 26-07-2020 18:45 | 31.82
Northern | K1 | TRIPPING-2020-KED-451 | 0242/20200728/039 | Kedah | Jitra | 11kV | Substation | 28-07-2020 22:25 | PPU DARULAMAN 4K5 | PPU DARULAMAN 4K5 | RUMAH KEDAI 50 UNIT | Transformer IR Test - HV-LV IR Failed | Partly Environment | Transformer | TRANSFORMER | 28-07-2020 22:27 | 28-07-2020 22:55 | 28 |  |  |  | 29-07-2020 14:15 | 15.83
Northern | K1 | TRIPPING-2020-PLS-48 | 2610/20200729/048 | Perlis | Perlis | 11kV | Underground | 29-07-2020 03:39 | PMU CHUPING CB4 | PMU CHUPING CB4 | PMUCHUPING CB4 - PDB TMN DESA PAUH | Core Broken | Defective Manufacture | Cable | CABLE | 29-07-2020 03:42 | 29-07-2020 04:14 | 32 | 04-08-2020 23:05 | 07-08-2020 06:04 | 54 | 07-08-2020 06:25 | 218.77
Northern | K1 | TRIPPING-2020-PLS-49 | 2610/20200727/071 | Perlis | Perlis | 11kV | Overhead | 29-07-2020 05:01 | PMU CHUPING CB6 | FELDA CHUPING NO.2 KAN02699 CB1 | TAMAN FELDA CHUPING 1 - PBT ALFALFA | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 29-07-2020 05:03 | 29-07-2020 05:39 | 36 | 29-07-2020 19:03 | 30-07-2020 06:41 | 11 | 30-07-2020 02:51 | 21.83
Northern | K1 | TRIPPING-2020-PLS-52 | 2610/20200807/013 | Perlis | Perlis | 11kV | Underground | 07-08-2020 11:42 | PPU SHORUBBER CB3 | PDB KLG PADI MAJU KAN01040 CB1 | KILANG PADI MAJU - KG TEBUK, - PDB BONGOR KUDONG - P/E SPG CANTIK BANGUN | Overload | Partly Environment | ABC Conductor | CABLE | 07-08-2020 11:44 | 07-08-2020 12:07 | 23 | 09-08-2020 22:12, 09-08-2020 22:14 | 14-08-2020 03:12, 09-08-2020 22:30 | 101, 0 | 14-08-2020 03:21 | 159.65
Northern | K1 | TRIPPING-2020-KED-473 | 0242/20200808/011 | Kedah | Jitra | 11kV | Underground | 08-08-2020 17:00 | PPU PELUBANG PL3 | PDB SK PENGHULU HJ DARUS KJT00700 CB1 | PBT KG. MALAU-ALS - PLB KG. TENGAH | Failed, Shorted by Old External Damage | Partly Environment | Straight Through Joint | CABLE | 08-08-2020 17:05 | 08-08-2020 17:37 | 32 | 08-08-2020 19:53 | 09-08-2020 23:48 | 27 | 09-08-2020 23:59 | 30.98
Northern | K1 | TRIPPING-2020-PLS-53 | 2610/20200809/019 | Perlis | Perlis | 11kV | Underground | 09-08-2020 14:31 | PPU PADANG BESAR | RPA PADANG BESAR KAN02911 | KG MELAYU - RPA PADANG BESAR | Failed, Shorted by Old External Damage | Partly Environment | Straight Through Joint | CABLE | 09-08-2020 15:47 | 09-08-2020 15:49 | 2 | 10-08-2020 23:44, 16-08-2020 12:25 | 16-08-2020 10:57, 17-08-2020 13:37 | 131, 25 | 17-08-2020 14:00 | 191.48
Northern | K1 | TRIPPING-2020-PLS-54 | 2610/20200810/022 | Perlis | Perlis | 11kV | Underground | 10-08-2020 17:56 | PMU CHUPING CB8 | TAE HWA KAN00225 CB1 | PDB RPA CHUPING 1 - PDB RUMAH GERAI BKT KETERI | Core Broken | Defective Manufacture | Cable | CABLE | 10-08-2020 17:59 | 10-08-2020 18:42 | 43 | 13-08-2020 13:20, 06-09-2020 18:14 | 05-09-2020 13:39, 07-09-2020 08:42 | 552, 14 | 07-09-2020 08:58 | 663.03
Northern | K1 | TRIPPING-2020-PLS-55 | 2610/20200810/026 | Perlis | Perlis | 11kV | Underground | 10-08-2020 18:17 | PPU SHORUBBER CB8 | PDB SMPG ABI KAN00314 CB1 | PDB SMPG ABI - KUARI BATU TEONG CHAI | Core Broken | Defective Manufacture | Cable | CABLE | 10-08-2020 18:30 | 10-08-2020 18:45 | 15 | 13-08-2020 01:53 | 22-08-2020 09:58 | 224 | 22-08-2020 10:10 | 279.88
Northern | K1 | TRIPPING-2020-KED-478 | 0242/20200811/001 | Kedah | Jitra | 11kV | Underground | 11-08-2020 00:09 | PMU TANJUNG PAUH TP15 | PDB IBUSAWAT TELEKOM JTR-TLKOM KJT00460 CB1 | PDB TMN PASU - PDB MADA JITRA | Core Opened | Partly Environment | Cable | CABLE | 11-08-2020 00:01 | 11-08-2020 00:32 | 31 | 11-08-2020 16:54 | 26-09-2020 07:50 | 1094 | 26-09-2020 09:20 | 1113.18
Northern | K1 | TRIPPING-2020-PLS-56 | 2610/20200811/001 | Perlis | Perlis | 11kV | Underground | 11-08-2020 00:57 | PMU CHUPING CB1 | PMU CHUPING CB1 | PAT BAWAH BUKIT - PDB INFANTRI BATALION | Insulation Burnt | Poor Workmanship | Cable Termination | CABLE | 11-08-2020 00:59 | 11-08-2020 01:30 | 31 | 12-08-2020 22:29 | 20-08-2020 04:04 | 173 | 20-08-2020 04:52 | 219.92
Northern | K1 | TRIPPING-2020-PLS-57 | 2610/20200811/139 | Perlis | Perlis | 11kV | Underground | 11-08-2020 13:50 | PPU BUKIT KETERI 9K5 | PPU BUKIT KETERI 9K5 | PPUBUKIT KETERI 9K5 - RPA MATA AIR | Core Opened | Defective Manufacture | Cable | CABLE | 11-08-2020 13:56 | 11-08-2020 14:20 | 24 | 13-08-2020 00:52, 19-08-2020 11:38 | 19-08-2020 11:11, 20-08-2020 13:02 | 154, 25 | 20-08-2020 13:50 | 216
Northern | K1 | TRIPPING-2020-KED-481 | 0242/20200812/001 | Kedah | Jitra | 11kV | Substation | 12-08-2020 01:25 | PMU TANJUNG PAUH TP21 | PDB TMN GOLF 1 KJT00625 CB1 | PDB TMN SUASANA INDAH 1 - P/P WATER THEAM PARK | Cable Compartment - Cable Termination Bushing Crack | Partly Environment | RMU SF6 | CABLE | 12-08-2020 01:29 | 12-08-2020 01:54 | 25 | 13-08-2020 17:13 | 13-08-2020 23:25 | 6 | 14-08-2020 00:25 | 47
Northern | K1 | TRIPPING-2020-KED-490 | 0245/20200816/019 | Kedah | Kuala Nerang | 11kV | Underground | 16-08-2020 22:16 | PPU KUALA NERANG KN2 | A/R SEK MEN PEDU | PBT PADANG SETUL - PLB KG. TANJUNG LUAR |  |  |  | CABLE | 16-08-2020 22:17 | 16-08-2020 22:40 | 23 | 17-08-2020 09:11 | 18-08-2020 01:34 | 16 | 19-08-2020 16:50 | 66.57
Northern | K1 | TRIPPING-2020-PLS-59 | 2610/20200817/011 | Perlis | Perlis | 11kV | Underground | 17-08-2020 10:50 | PMU KANGAR CB6 | PMU KANGAR CB6 | PUSAT PERTAHANAN AWAM PERLIS - HTL SRI MALAYSIA KANGAR | Core Opened | Defective Manufacture | Cable | CABLE | 17-08-2020 10:55 | 17-08-2020 11:13 | 18 | 18-08-2020 22:16 | 04-09-2020 08:52 | 394 | 04-09-2020 09:14 | 430.4
Northern | K1 | TRIPPING-2020-PLS-60 | 2610/20200818/002 | Perlis | Perlis | 11kV | Underground | 18-08-2020 02:32 | PMU KUALA PERLIS CB7 | PMU KUALA PERLIS CB7 | PMUKUALA PERLIS CB7 - PDB PERLIS MARINE | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 18-08-2020 02:36 | 18-08-2020 03:15 | 39 | 18-08-2020 03:55 | 19-08-2020 20:31 | 40 | 19-08-2020 21:05 | 42.55
Northern | K1 | TRIPPING-2020-PLS-61 | 2610/20200821/002 | Perlis | Perlis | 11kV | Overhead | 21-08-2020 05:57 | PPU SHORUBBER CB5 | PPU SHORUBBER CB5 | PPUSHORUBBER CB5 - PBT KG. SIAM | Overload | Partly Environment | ABC Conductor | CABLE | 21-08-2020 05:59 | 21-08-2020 06:30 | 31 | 21-08-2020 07:07, 27-09-2020 11:53 | 27-09-2020 10:38, 29-09-2020 11:48 | 891, 47 | 01-10-2020 09:47 | 987.83
Northern | K1 | TRIPPING-2020-PLS-62 | 2610/20200823/004 | Perlis | Perlis | 11kV | Underground | 23-08-2020 11:23 | PMU CHUPING CB1 | PMU CHUPING CB1 | PDB INFANTRI BATALION - LOGISTIK | Damaged, Shorted by Third Party Dug Up | Unavoidable Accident | Cable | CABLE | 23-08-2020 11:25 | 23-08-2020 12:03 | 38 | 24-08-2020 13:05 | 30-08-2020 00:10 | 131 | 30-08-2020 00:27 | 157.07
Northern | K1 | TRIPPING-2020-KED-514 | 0242/20200829/025 | Kedah | Jitra | 11kV | Overhead | 29-08-2020 18:11 | PPU CHANGLOON CL5 | PPU CHANGLOON CL5 | PATOD KG BARU SINTOK 2 - TMN SEMARAK API | Overload | Partly Environment | ABC Conductor | OVERHEAD LINES | 29-08-2020 18:20 | 29-08-2020 19:00 | 40 | 30-08-2020 10:47, 30-08-2020 15:37 | 30-08-2020 13:02, 30-08-2020 22:44 | 2, 7 | 30-08-2020 22:19 | 28.13
Northern | K1 | TRIPPING-2020-KED-516 | 0242/20200830/011 | Kedah | Jitra | 11kV | Underground | 30-08-2020 11:54 | PPU CHANGLOON CL3 | PPU CHANGLOON CL3 | S/S SG. KELIAN - PAT RUMAH PAM JALAN KODIANG | Insulation Failed, Shorted by Old External Damage | Partly Environment | Cable | CABLE | 30-08-2020 11:57 | 30-08-2020 12:20 | 23 | 30-08-2020 13:08 | 31-08-2020 02:19 | 13 | 31-08-2020 02:35 | 14.68
Northern | K1 | TRIPPING-2020-PLS-63 | 2610/20200830/026 | Perlis | Perlis | 11kV | Underground | 30-08-2020 23:34 | PMU CHUPING CB4 | PDB TMN DESA PAUH KAN00923 CB1 | TMN DESA PAUH - PDB RPA PEKAN PAUH | Failed, Shorted by Old External Damage | Partly Environment | Straight Through Joint | CABLE | 30-08-2020 23:34 | 31-08-2020 00:05 | 31 | 04-09-2020 22:23 | 04-10-2020 16:30 | 714 | 04-10-2020 16:47 | 833.22
Northern | K1 | TRIPPING-2020-KED-531 | 0242/20200904/020 | Kedah | Jitra | 11kV | Underground | 04-09-2020 09:18 | PPU DARULAMAN 3K5 | PPU DARULAMAN 3K5 | PDB SK MALAU - PATOD KG. PENIA | Core Opened | Defective Manufacture | Cable | CABLE | 04-09-2020 09:22 | 04-09-2020 09:43 | 21 | 04-09-2020 15:03 | 04-09-2020 16:35 | 1 | 05-09-2020 20:33 | 35.25
Northern | K1 | TRIPPING-2020-PLS-64 | 2610/20200904/013 | Perlis | Perlis | 11kV | Underground | 04-09-2020 10:12 | PPU BUKIT KETERI SELATAN 6L5 | MPPU ABI 31 | KELAB GOLF PUTRA - KUARI SYED OMAR | Damaged, Shorted by Third Party Dug Up | Improper Laying | Cable | CABLE | 04-09-2020 11:00 |  | 0 | 04-09-2020 23:45 | 01-10-2020 13:34 | 637 | 01-10-2020 13:48 | 651.6
Northern | K1 | TRIPPING-2020-PLS-65 | 2610/20200909/026 | Perlis | Perlis | 11kV | Underground | 09-09-2020 17:46 | PPU SHORUBBER CB3 | PDB MIEL KUKUM JEJAWI KAN00733 CB1 | PATOD SMPG SERDANG - PDB KLG PADI MAJU | Core Opened | Partly Environment | Cable | CABLE | 09-09-2020 17:55 | 09-09-2020 18:19 | 24 | 12-09-2020 00:25 | 25-09-2020 08:56 | 320 | 25-09-2020 10:40 | 376.9
Northern | K1 | TRIPPING-2020-PLS-67 | 2610/20200912/027 | Perlis | Perlis | 11kV | Underground | 12-09-2020 18:23 | PMU KANGAR CB16 | TAMAN JALI KAN02326 | TMN BUKIT KAYA INDAH - PBT BUKIT KAYA |  |  |  | CABLE | 12-09-2020 19:00 | 12-09-2020 19:28 | 28 | 14-09-2020 22:13 | 16-09-2020 07:25 | 33 | 16-09-2020 07:37 | 85.23
Northern | K1 | TRIPPING-2020-KED-547 | 0242/20200913/011 | Kedah | Jitra | 11kV | Underground | 13-09-2020 08:53 | PPU DARULAMAN 3K5 | PPU DARULAMAN 3K5 | PATOD KG. PENIA - PDB SK MALAU | Damaged, Soil Movement | Under Investigation | Cable | CABLE | 13-09-2020 08:57 | 13-09-2020 09:10 | 13 | 13-09-2020 17:07 | 15-09-2020 10:00 | 40 | 15-09-2020 11:00 | 50.12
Northern | K1 | TRIPPING-2020-KED-548 | 0242/20200914/013 | Kedah | Jitra | 11kV | Underground | 14-09-2020 10:43 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01798 CB1 | PDB LOJI PENAPIS AIR - PBT KG. JERAGAN | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 14-09-2020 10:45 | 14-09-2020 11:01 | 16 | 14-09-2020 14:41 | 15-09-2020 03:55 | 13 | 15-09-2020 04:16 | 17.55
Northern | K1 | TRIPPING-2020-PLS-69 | 2610/20200914/097 | Perlis | Perlis | 11kV | Underground | 14-09-2020 23:19 | PMU KANGAR CB16 | SSU GIANT KGAR KAN02771 | PDB SK RAJA SYED ALWI - PDT PETRONAS NGV PERLIS-VVIP | Failed, Shorted by Water Ingress | Poor Workmanship | Straight Through Joint | CABLE | 14-09-2020 23:22 | 14-09-2020 23:50 | 28 | 15-09-2020 23:40 | 20-09-2020 01:06 | 97 | 20-09-2020 01:27 | 122.13
Northern | K1 | TRIPPING-2020-PLS-70 | 2610/20200916/008 | Perlis | Perlis | 11kV | Substation | 16-09-2020 07:33 | PPU PADANG BESAR CB12 | RPA PADANG BESAR KAN02911 |  | Contact Loose / Open by Strong Wind | Partly Environment | Link Switch | TRANSIENT | 16-09-2020 08:45 | 16-09-2020 09:35 | 50 |  |  |  | 16-09-2020 09:40 | 2.12
Northern | K1 | TRIPPING-2020-KED-556 | 0242/20200918/019 | Kedah | Jitra | 11kV | Underground | 18-09-2020 04:41 | PPU CHANGLOON CL3 | PPU CHANGLOON CL3 | PAT SG. KELIAN - PAT RUMAH PAM JALAN KODIANG | Core Opened | Partly Environment | Cable | CABLE | 18-09-2020 04:45 | 18-09-2020 04:59 | 14 | 18-09-2020 11:28 | 19-09-2020 03:58 | 16 | 19-09-2020 04:16 | 23.58
Northern | K1 | TRIPPING-2020-KED-564 | 0245/20200919/013 | Kedah | Kuala Nerang | 11kV | Overhead | 19-09-2020 17:51 | PPU KUALA NERANG KN4 | PDB SMK KUALA NERANG KKN00054 CB1 | PBT PONG MANIS - S/S BUKIT NAMBUA | Opened by Vandals | Partly Environment | ABC Conductor | CABLE | 19-09-2020 18:05 | 19-09-2020 18:50 | 45 | 19-09-2020 21:48 | 20-09-2020 21:37 | 23 | 20-09-2020 22:30 | 28.65
Northern | K1 | TRIPPING-2020-KED-572 | 0242/20200922/119 | Kedah | Jitra | 11kV | Underground | 22-09-2020 19:08 | PPU DARULAMAN 10K5 | PPU DARULAMAN 10K5 |  | Core Opened | Partly Environment | Cable | CABLE | 22-09-2020 19:11 | 22-09-2020 19:25 | 14 |  |  |  | 22-09-2020 21:39 | 2.52
Northern | K1 | TRIPPING-2020-PLS-71 | 2610/20200926/008 | Perlis | Perlis | 11kV | Underground | 26-09-2020 10:32 | PPU SHORUBBER CB10 | BEHOR MENTALOON KAN00976 CB1 |  | Core Opened | Defective Manufacture | Cable | OTHER | 26-09-2020 10:38 | 26-09-2020 10:58 | 20 |  |  |  | 26-09-2020 11:22 | 0.83
Northern | K1 | TRIPPING-2020-KED-580 | 0245/20200926/018 | Kedah | Kuala Nerang | 11kV | Underground | 26-09-2020 16:35 | PPU MINI PPU L/AIR PDG SANAI LA3 | LDG SG SERAYA KKN00773 CB1 | LDG SG SERAYA - PDT SMPG TIGA DURIAN BURUNG | Failed, Shorted by Corrosive Evmnt | Partly Environment | Transition Joint | CABLE | 26-09-2020 16:40 | 26-09-2020 17:20 | 40 | 26-09-2020 22:50 | 28-09-2020 01:48 | 26 | 28-09-2020 03:48 | 35.22
Northern | K1 | TRIPPING-2020-KED-582 | 0240/2020927/001 | Kedah | Jitra | 11kV | Substation | 27-09-2020 04:24 | PPU JERLUN SJ2 | KLG PROSES UDANG KJT01687 | SS SAMAK | CB Compartment - Tank Corroded | Partly Environment | Circuit Breaker | SWITCHGEAR | 27-09-2020 04:26 | 27-09-2020 05:25 | 59 | 28-09-2020 11:46 | 30-09-2020 21:41 | 57 | 30-09-2020 22:18 | 89.9
Northern | K1 | TRIPPING-2020-KED-584 | 0245/20200927/010 | Kedah | Kuala Nerang | 11kV | Underground | 27-09-2020 19:18 | PPU NAKA 6K5 | SSBT KG. CHANDING KKN00416 CB1 | PBT KG. PADANG - PBT SG. KAP2 | Failed, Shorted by Corrosive Evmnt | Partly Environment | Straight Through Joint | CABLE | 27-09-2020 19:28 | 27-09-2020 19:48 | 20 | 27-09-2020 23:52 | 28-09-2020 21:17 | 21 | 29-09-2020 21:50 | 50.53
Northern | K1 | TRIPPING-2020-PLS-72 | 2610/20201001/010 | Perlis | Perlis | 11kV | Underground | 01-10-2020 07:48 | PMU KANGAR CB14 | PMU KANGAR CB14 | PDB DRAGON & PHEONIX 1 - ADVANCE CHICKEN | Failed, Shorted by Water Ingress | Poor Workmanship | Straight Through Joint | CABLE | 01-10-2020 07:53 | 01-10-2020 08:09 | 16 | 01-10-2020 22:20 | 07-10-2020 12:05 | 133 | 07-10-2020 12:35 | 148.78
Northern | K1 | TRIPPING-2020-KED-591 | 0242/20201002/003 | Kedah | Jitra | 11kV | Underground | 02-10-2020 04:41 | PMU TANJUNG PAUH TP9 | TMN DESA TANJUNG KJT19017 CB1 | PDB SM ALOR BIAK - PAT KOTA RENTANG | Core Opened | Partly Environment | Cable | CABLE | 02-10-2020 04:59 | 02-10-2020 05:44 | 45 | 02-10-2020 21:23 | 03-10-2020 13:12 | 15 | 03-10-2020 13:12 | 32.52
Northern | K1 | TRIPPING-2020-KED-592 | 0292/20201002/063 | Kedah | Jitra | 11kV | Underground | 02-10-2020 14:54 | PMU TANJUNG PAUH TP15 | PMU TANJUNG PAUH TP15 | PMUTANJUNG PAUH TP15 - PDB KAWAN SUPERMARKET | Failed, Shorted by Old External Damage | Partly Environment | Straight Through Joint | CABLE | 02-10-2020 15:00 | 02-10-2020 15:15 | 15 | 02-10-2020 16:55 | 04-10-2020 04:45 | 35 | 05-10-2020 23:50 | 80.93
Northern | K1 | TRIPPING-2020-PLS-73 | 2610/20201003/004 | Perlis | Perlis | 11kV | Underground | 03-10-2020 07:21 | PPU PADANG BESAR CB2 | PDB PEKAN KAKI BUKIT KAN00140 |  | Damaged by Animal | Partly Environment | Drop Out Fuse | TRANSIENT | 03-10-2020 07:30 |  | 0 |  |  |  | 03-10-2020 10:25 | 3.07
Northern | K1 | TRIPPING-2020-KED-605 | 0242/20201008/002 | Kedah | Jitra | 11kV | Underground | 08-10-2020 06:16 | PPU JERLUN SJ4 | KLG BERAS SUPREME KJT01676 | SM ALOR BIAK - PAT KOTA RENTANG | Failed, Shorted by Old External Damage | Partly Environment | Straight Through Joint |  | 08-10-2020 06:30 | 08-10-2020 06:57 | 27 | 08-10-2020 09:14 | 09-10-2020 05:43 | 20 | 09-10-2020 05:43 | 23.45
Northern | K1 | TRIPPING-2020-KED-614 | 0242/20201009/015 | Kedah | Jitra | 11kV | Underground | 09-10-2020 12:18 | PPU UUM SINTOK ST5 | S/S KLJ PERTANIAN BKT TANGGA KJT01848 CB1 | PLB FELDA BUKIT TANGGA - PATOD KG. BARU PADONG |  |  |  | CABLE | 09-10-2020 12:20 | 09-10-2020 13:00 | 40 | 08-11-2020 00:49 | 08-11-2020 06:31 | 5 | 08-11-2020 06:57 | 714.65
Northern | K1 | TRIPPING-2020-KED-622 | 0242/20201013/060 | Kedah | Jitra | 11kV | Underground | 13-10-2020 19:09 | PPU DARULAMAN 13K5 | PPU DARULAMAN 13K5 | TMN DESA HALBAN - PDB SM TANGJUNG PAUH | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 13-10-2020 19:11 | 13-10-2020 19:30 | 19 | 14-10-2020 02:05, 14-10-2020 01:12 | 14-10-2020 15:52, 14-10-2020 21:34 | 13, 20 | 14-10-2020 16:10 | 21.02
Northern | K1 | TRIPPING-2020-PLS-76 | 2610/20201014/005 | Perlis | Perlis | 11kV | Underground | 14-10-2020 03:38 | PPU SHORUBBER CB4 | PVCB TMN JALI KAN02329 CB1 | PDB TMN KEMAJUAN 1 - PDB TMN KEMAJUAN 2 | Core Opened | Defective Manufacture | Cable | CABLE | 14-10-2020 03:44 | 14-10-2020 04:16 | 32 | 14-10-2020 22:48 | 25-10-2020 14:18 | 255 | 25-10-2020 15:18 | 275.67
Northern | K1 | TRIPPING-2020-PLS-77 | 2610/20201017/011 | Perlis | Perlis | 11kV | Underground | 17-10-2020 14:25 | PMU CHUPING CB1 | PLB KAJI CUACA KAN00789 CB1 | KOMP KEBAJIKAN MASYARAKAT-VVIP - PAT SG. MATI | Damaged, Shorted by Third Party Dug Up | Improper Laying | Cable | CABLE | 17-10-2020 14:28 | 17-10-2020 14:54 | 26 | 18-10-2020 22:11 | 21-10-2020 02:29 | 52 | 21-10-2020 02:54 | 84.48
Northern | K1 | TRIPPING-2020-KED-632 | 0242/20201018/023 | Kedah | Jitra | 11kV | Underground | 18-10-2020 17:57 | PMU TANJUNG PAUH TP4 | PMU TANJUNG PAUH TP4 | PMUTANJUNG PAUH TP4 - R/AWAM TG PAUH | Failed, Shorted by Water Ingress | Under Investigation | Straight Through Joint | CABLE | 18-10-2020 18:00 | 18-10-2020 18:00 | 0 | 18-10-2020 18:43 | 19-10-2020 07:12 | 12 | 19-10-2020 07:21 | 13.4
Northern | K1 | TRIPPING-2020-PLS-78 | 2610/20201024/043 | Perlis | Perlis | 11kV | Underground | 24-10-2020 13:18 | PPU BUKIT KETERI 7K5 | PDB TMN BESERI JAYA KAN00178 CB1 | PBT LMBH BIAK - PDB TMN BESERI MURNI-VVIP | Failed, Shorted by Old External Damage | Partly Environment | Straight Through Joint | CABLE | 24-10-2020 13:19 | 24-10-2020 13:50 | 31 | 26-10-2020 22:32 | 04-11-2020 08:36 | 202 | 04-11-2020 08:58 | 259.67
Northern | K1 | TRIPPING-2020-KED-648 | 0242/20201026/004 | Kedah | Jitra | 11kV | Overhead | 26-10-2020 09:04 | PPU CHANGLOON CL2 | PDB TMN MERBAU KJT18965 CB1 | PDB KG. TRADISI NO.2 - PDB TMN SEMARAK API | Opened by Vandals | Partly Environment | ABC Conductor | CABLE | 26-10-2020 09:12 | 26-10-2020 09:38 | 26 | 26-10-2020 19:06 | 05-11-2020 15:15 | 236 | 05-11-2020 16:53 | 247.82
Northern | K1 | TRIPPING-2020-KED-649 | 0245/20201026/015 | Kedah | Kuala Nerang | 11kV | Underground | 26-10-2020 15:10 | PPU NAKA 6K5 | A/R KG CHANDING | PLB LOJI AIR NAMI - KG BARU NAMI | Damaged, Shorted by Third Party Dug Up | Improper Laying | Cable | CABLE | 26-10-2020 15:13 | 26-10-2020 15:20 | 7 | 26-10-2020 17:25 | 28-10-2020 05:31 | 36 | 28-10-2020 05:45 | 38.58
Northern | K1 | TRIPPING-2020-KED-651 | 0242/20201027/008 | Kedah | Jitra | 11kV | Underground | 27-10-2020 12:03 | PMU TANJUNG PAUH TP9 | PMU TANJUNG PAUH TP9 | PDB MACRO DIMENSION - PDB SMK BDR DARUL AMAN | Damaged, Shorted by Third Party Dug Up | Unavoidable Accident | Cable | CABLE | 27-10-2020 12:07 | 27-10-2020 12:30 | 23 | 28-10-2020 13:26 | 28-10-2020 22:42 | 9 | 29-10-2020 00:57 | 36.9
Northern | K1 | TRIPPING-2020-PLS-79 | 2610/20201027/021 | Perlis | Perlis | 11kV | Underground | 27-10-2020 14:36 | PPU PADANG BESAR CB2 | PEKAN SAYUR KAN00131 | WANGMU - KLG TH MINERAL | Insulation Failed, Shorted by Old External Damage | Partly Environment | Cable Termination | CABLE | 27-10-2020 14:54 | 27-10-2020 15:45 | 51 | 31-10-2020 11:12 | 31-10-2020 23:58 | 12 | 01-11-2020 00:14 | 105.63
Northern | K1 | TRIPPING-2020-KED-654 | 0242/20201027/045 | Kedah | Jitra | 11kV | Underground | 27-10-2020 18:33 | PMU BUKIT KAYU HITAM BKH8 | PMU BUKIT KAYU HITAM BKH8 | PBT BATU 25 - TMN SEMARAK API NO 2 | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 27-10-2020 18:38 | 27-10-2020 19:02 | 24 | 27-10-2020 23:54 | 30-10-2020 18:27 | 66 | 30-10-2020 00:00 | 53.45
Northern | K1 | TRIPPING-2020-KED-670 | 0242/20201103/018 | Kedah | Jitra | 11kV | Overhead | 03-11-2020 16:14 | PPU JERLUN SJ1 | SEK MEN KEB AYER HITAM KJT19066 | PLB PERMATANG KERPAN - SMK AYER ITAM | Failed, Shorted by Old External Damage | Partly Environment | Straight Through Joint | CABLE | 03-11-2020 16:47 | 03-11-2020 17:32 | 45 | 05-11-2020 00:15 | 05-11-2020 17:54 | 17 | 05-11-2020 18:24 | 50.17
Northern | K1 | TRIPPING-2020-PLS-80 | 2610/20201110/012 | Perlis | Perlis | 11kV | Substation | 10-11-2020 12:38 | PPU SHORUBBER CB3 | PDB MIEL KUKUM JEJAWI KAN00731 CB1 | PDB MIEL KUKUM JEJAWI - PDB MIE JEJAWI | Pressure Test Failure | Partly Environment | Circuit Breaker | SWITCHGEAR | 10-11-2020 12:42 | 10-11-2020 13:00 | 18 | 13-11-2020 17:15 | 14-11-2020 07:04 | 13 | 14-11-2020 19:01 | 102.38
Northern | K1 | TRIPPING-2020-PLS-81 | 2610/20201112/017 | Perlis | Perlis | 11kV | Underground | 12-11-2020 15:59 | PPU PADANG BESAR CB7 | PPU PADANG BESAR CB7 | PPUPADANG BESAR CB7 - PVCB QTRS KTMB | Damaged, Shorted by Third Party Dug Up | Unavoidable Accident | Cable | CABLE | 12-11-2020 16:05 |  | 0 | 12-11-2020 22:13 | 13-11-2020 09:01 | 10 | 13-11-2020 09:43 | 17.73
Northern | K1 | TRIPPING-2020-KED-692 | 0242/20201112/028 | Kedah | Jitra | 11kV | Underground | 12-11-2020 19:51 | PPU KODIANG KD6 | PPU KODIANG KD6 | PLB PEKAN KODIANG - PLB LPN KODIANG | Failed, Shorted by Old External Damage | Partly Environment | Straight Through Joint | CABLE | 12-11-2020 19:58 | 12-11-2020 20:30 | 32 | 13-11-2020 17:58 | 14-11-2020 05:29 | 11 | 14-11-2020 06:05 | 34.23
Northern | K1 | TRIPPING-2020-PLS-83 | 2610/20201114/007 | Perlis | Perlis | 11kV | Underground | 14-11-2020 13:50 | PPU BUKIT KETERI 7K5 | PDB TMN BESERI JAYA KAN00179 CB1 | PLB JALAN LENCONGAN - CCRC BKT CHABANG | Core Opened | Under Investigation | Cable | CABLE | 14-11-2020 13:53 | 14-11-2020 14:20 | 27 | 15-11-2020 09:55 | 18-11-2020 07:44 | 69 | 18-11-2020 08:16 | 90.43
Northern | K1 | TRIPPING-2020-KED-707 | 0245/20201117/002 | Kedah | Kuala Nerang | 11kV | Underground | 17-11-2020 06:44 | PPU NAKA 1K5 | PPU NAKA 1K5 | PBT KG. NAHAN - | Core Opened | Partly Environment | Cable | TRANSIENT | 17-11-2020 06:52 | 17-11-2020 07:15 | 23 |  |  |  | 18-11-2020 13:10 | 30.43
Northern | K1 | TRIPPING-2020-PLS-85 | 2610/20201118/019 | Perlis | Perlis | 11kV | Underground | 18-11-2020 16:12 | PMU KUALA PERLIS CB6 | PDB TOP FOOD KAN01202 CB1 | PDB HTL PTRA BRASMNA KLA PRLIS - PDB KOMP LKIM K.PERLIS | Core Opened | Defective Manufacture | Cable | CABLE | 18-11-2020 16:17 | 18-11-2020 16:45 | 28 | 19-11-2020 22:52 | 26-11-2020 08:10 | 153 | 26-11-2020 08:30 | 184.3
Northern | K1 | TRIPPING-2020-PLS-86 | 2610/20201118/037 | Perlis | Perlis | 11kV | Underground | 18-11-2020 16:19 | PMU KANGAR CB10 | FLAT POLIS KANGAR KAN00517 | TOK PELUKA - PANGSAPURI SRI SENA | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 18-11-2020 17:04 | 18-11-2020 17:13 | 9 | 18-11-2020 18:03 | 19-11-2020 05:42 | 11 | 19-11-2020 05:45 | 13.43
Northern | K1 | TRIPPING-2020-PLS-87 | 2610/20201119/004 | Perlis | Perlis | 11kV | Underground | 19-11-2020 05:29 | PPU SIMPANG EMPAT CB4 | PPU SIMPANG EMPAT CB4 |  | Terminal Shorted by Animal / Insects | Partly Environment | Drop Out Fuse | TRANSIENT | 19-11-2020 05:35 | 19-11-2020 06:15 | 40 |  |  |  | 19-11-2020 08:12 | 2.72
Northern | K1 | TRIPPING-2020-KED-713 | 0245/20201119/011 | Kedah | Kuala Nerang | 11kV | Underground | 19-11-2020 19:31 | PPU KUALA NERANG KN1 | PPU KUALA NERANG KN1 | PLB TANJUNG SEBERANG - PBT KG. PISANG 2 | Core Opened | Partly Environment | Cable | SWITCHGEAR | 19-11-2020 19:34 | 19-11-2020 19:47 | 13 | 20-11-2020 12:42 | 21-11-2020 02:32 | 13 | 21-11-2020 03:31 | 32
Northern | K1 | TRIPPING-2020-PLS-88 | 2610/20201125/021 | Perlis | Perlis | 11kV | Underground | 25-11-2020 05:57 | PPU SIMPANG EMPAT CB4 | PPU SIMPANG EMPAT CB4 |  |  |  |  | OTHER | 25-11-2020 06:03 | 25-11-2020 07:00 | 57 |  |  |  | 25-11-2020 08:23 | 2.43
Northern | K1 | TRIPPING-2020-PLS-89 | RE/2610/20201127/PLS/089 | Perlis | Perlis | 11kV | Underground | 27-11-2020 16:20 | PPU UNIMAP GIS 1K5 | SSD UNIMAP ULU PAUH KAN02786 | RE GETSOL |  |  |  | OTHER | 27-11-2020 16:58 | 27-11-2020 16:58 | 0 | 27-11-2020 17:55 | 23-12-2020 02:01 | 608 | 28-11-2020 16:50 | 24.5
Northern | K1 | TRIPPING-2020-PLS-91 | 2610/20201129/008 | Perlis | Perlis | 11kV | Underground | 29-11-2020 07:44 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 | PDB JPJ JEJAWI-VVIP - PDB SEDC TMN JEJAWI-VVIP |  |  |  | CABLE | 29-11-2020 07:45 | 29-11-2020 08:10 | 25 | 29-11-2020 23:24 | 07-12-2020 07:46 | 176 | 07-12-2020 07:59 | 192.25
Northern | K1 | TRIPPING-2020-KED-753 | 0245/20201204/003 | Kedah | Kuala Nerang | 11kV | Underground | 04-12-2020 10:26 | PPU KUALA NERANG KN5 | PPU KUALA NERANG KN5 | PLB RMU PPU KUALA NERANG - PDB TMN AKASIA | Core Opened | Partly Environment | Cable | CABLE | 04-12-2020 10:28 | 04-12-2020 10:50 | 22 | 04-12-2020 15:53 | 05-12-2020 04:46 | 12 | 05-12-2020 05:10 | 18.73
Northern | K1 | TRIPPING-2020-KED-754 | 0245/20201204/003 | Kedah | Kuala Nerang | 11kV | Underground | 04-12-2020 10:30 | PPU KUALA NERANG KN1 | A/R TG SEBERANG |  | Core Opened | Partly Environment | Cable | OTHER | 04-12-2020 10:35 | 04-12-2020 12:00 | 85 |  |  |  | 04-12-2020 12:57 | 2.45
Northern | K1 | TRIPPING-2020-KED-755 | 0245/20201204/034 | Kedah | Kuala Nerang | 11kV | Underground | 04-12-2020 12:33 | PPU KUALA NERANG KN3 | A/R KG. TENGAH | PATOD KG.BUKIT PERIK - PBT KG. PERIK |  |  |  | CABLE | 04-12-2020 13:00 | 04-12-2020 13:17 | 17 | 04-12-2020 16:30 | 05-12-2020 05:24 | 12 | 05-12-2020 06:06 | 17.55
Northern | K1 | TRIPPING-2020-PLS-92 | 2610/20201205/001 | Perlis | Perlis | 11kV | Underground | 05-12-2020 02:31 | PMU KUALA PERLIS CB5 | PDB TMN BUMITA KAN00595 CB1 | TMN SIMPANG INDAH - TMN KAYANG PERMAI | Core Opened | Defective Manufacture | Cable | CABLE | 05-12-2020 02:39 | 05-12-2020 03:02 | 23 | 06-12-2020 23:25 | 15-12-2020 03:10 | 195 | 15-12-2020 03:20 | 240.82
Northern | K1 | TRIPPING-2020-KED-763 | 0242/20201206/014 | Kedah | Jitra | 11kV | Underground | 06-12-2020 15:41 | PMU TANJUNG PAUH TP15 | PDB IBUSAWAT TELEKOM JTR-TLKOM KJT00460 | PDB MADA JITRA - PDB TMN SETIA JAYA | Core Opened | Partly Environment | Cable | CABLE | 06-12-2020 15:42 | 06-12-2020 15:48 | 6 | 07-12-2020 10:30 | 08-12-2020 05:14 | 18 | 08-12-2020 05:35 | 37.9
Northern | K1 | TRIPPING-2020-KED-764 | 0245/20201206/052 | Kedah | Kuala Nerang | 11kV | Underground | 06-12-2020 21:46 | PPU KUALA NERANG KN4 | PDB SMK KUALA NERANG KKN00054 CB1 |  |  |  |  | OTHER | 06-12-2020 21:48 | 06-12-2020 21:56 | 8 |  |  |  | 06-12-2020 23:15 | 1.48
Northern | K1 | TRIPPING-2020-PLS-93 | 2610/20201211/005 | Perlis | Perlis | 11kV | Underground | 11-12-2020 09:29 | PMU KUALA PERLIS CB5 | PDB TMN BUMITA KAN00595 CB1 |  | Core Opened | Defective Manufacture | Cable | TRANSIENT | 11-12-2020 09:30 | 11-12-2020 10:10 | 40 |  |  |  | 11-12-2020 11:27 | 1.97
Northern | K1 | TRIPPING-2020-KED-781 | 0240/20201212/058 | Kedah | Kuala Nerang | 11kV | Underground | 12-12-2020 16:00 | PPU NAKA 4K5 | PPU NAKA 4K5 | KUBANG JULOK |  |  |  | OTHER | 12-12-2020 16:02 | 12-12-2020 16:19 | 17 |  |  |  | 12-12-2020 17:47 | 1.78
Northern | K1 | TRIPPING-2020-PLS-94 | 2610/20201214/070 | Perlis | Perlis | 11kV | Underground | 14-12-2020 20:59 | PMU KUALA PERLIS CB8 | PMU KUALA PERLIS CB8 | PMU KUALA PERLIS CB8 - PDB FRIENDLY WAY FROZEN |  |  |  | CABLE | 14-12-2020 21:02 | 14-12-2020 21:22 | 20 | 15-12-2020 20:34 | 16-12-2020 11:34 | 15 | 17-12-2020 11:01 | 62.03
Northern | K1 | TRIPPING-2020-PLS-95 | 2610/20201214/185 | Perlis | Perlis | 11kV | Underground | 14-12-2020 22:41 | PMU KUALA PERLIS CB6 | PDB AMAN FISHMEAL KAN00623 CB1 | PDB AMAN FISHMEAL - S/S BANGSAL LEBAH | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 14-12-2020 22:45 | 14-12-2020 22:45 | 0 | 11-01-2021 11:21, 11-01-2021 22:30 | 11-01-2021 21:35, 12-01-2021 05:14 | 10, 6 | 12-01-2021 05:42 | 679.02
Northern | K1 | TRIPPING-2020-PLS-96 | 2610/20201216/028 | Perlis | Perlis | 11kV | Underground | 16-12-2020 04:59 | PPU PADANG BESAR CB10 | UKK PADANG BESAR KAN00047 | CHECK POINT - BATU BERTANGKUP | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 16-12-2020 05:20 | 16-12-2020 05:55 | 35 | 16-12-2020 23:13 | 02-01-2021 06:19 | 391 | 02-01-2021 06:42 | 409.72
Northern | K1 | TRIPPING-2020-PLS-97 | 2610/20201217/013 | Perlis | Perlis | 11kV | Underground | 17-12-2020 11:19 | PPU SIMPANG EMPAT CB6 | PPU SIMPANG EMPAT CB6 | PDB RUMAH KEDAI BOHOR MALI - PDB KLG BERAS DIBOK(BARU) | Core Broken | Defective Manufacture | Cable | CABLE | 17-12-2020 11:19 | 17-12-2020 11:44 | 25 | 17-12-2020 14:12, 17-12-2020 23:54 | 17-12-2020 19:14, 18-12-2020 11:58 | 5, 12 | 18-12-2020 12:18 | 24.98
Northern | K1 | TRIPPING-2020-KED-819 | 0245/20201226/005 | Kedah | Kuala Nerang | 11kV | Underground | 26-12-2020 15:09 | PPU KUALA NERANG KN2 | A/R SEK MEN PEDU | PBT KG. BUNGA - R/PAM KG BKT SENA | Core Opened | Partly Environment | Cable | CABLE | 26-12-2020 15:10 | 26-12-2020 15:24 | 14 | 26-12-2020 21:02 | 27-12-2020 22:46 | 25 | 28-12-2020 00:06 | 32.95
Northern | K1 | TRIPPING-2020-PLS-98 | 2610/20201230/001 | Perlis | Perlis | 11kV | Underground | 30-12-2020 06:58 | PPU SHORUBBER CB5 | PPU SHORUBBER CB5 | PBT KG. SIAM - BEHOR MENTALOON |  |  |  | CABLE | 30-12-2020 07:03 | 30-12-2020 07:30 | 27 | 30-12-2020 20:42 | 02-01-2021 00:57 | 52 | 02-01-2021 01:21 | 66.38
Northern | K1 | TRIPPING-2021-PLS-1 | 2610/20210102/031 | Perlis | Perlis | 11kV | Underground | 02-01-2021 14:53 | PMU CHUPING CB8 | TAE HWA KAN00225 CB1 | PDB RPA CHUPING 1 - PDB RUMAH GERAI BKT KETERI | Core Broken | Defective Manufacture | Cable | CABLE | 02-01-2021 14:54 | 02-01-2021 15:22 | 28 | 03-01-2021 23:14, 19-01-2021 17:40 | 19-01-2021 16:51, 24-01-2021 16:05 | 377, 118 | 24-01-2021 16:15 | 529.37
Northern | K1 | TRIPPING-2021-PLS-2 | 2610/20210102/069 | Perlis | Perlis | 11kV | Underground | 02-01-2021 18:15 | PMU KANGAR CB11 | PMU KANGAR CB11 | PDB MKMH SYARIAH - PDB HOSPITAL BARU KANGAR | Damaged, Shorted by Third Party Dug Up | Under Investigation | Cable | CABLE | 02-01-2021 18:22 | 02-01-2021 18:30 | 8 | 04-01-2021 22:19 | 09-01-2021 13:59 | 111 | 09-01-2021 14:24 | 164.15
Northern | K1 | TRIPPING-2021-KED-6 | 0245/20210105/024 | Kedah | Jitra | 11kV | Overhead | 05-01-2021 06:46 | PPU KUALA NERANG KN4 | PDB PEKAN KUALA NERANG KKN00011 CB1 | PBT KG. SEMELIANG-VVIP - HOSPITAL K/NERANG | Opened by Vandals | Act of Vandalism | ABC Conductor | CABLE | 05-01-2021 09:59 | 05-01-2021 10:13 | 14 | 05-01-2021 19:12 | 06-01-2021 23:30 | 28 | 06-01-2021 23:50 | 41.07
Northern | K1 | TRIPPING-2021-PLS-3 | 2610/20210105/103 | Perlis | Perlis | 11kV | Underground | 05-01-2021 20:40 | PPU PADANG BESAR CB9 | PDB TITI TINGGI KAN00091 CB1 | PBT BUKIT CABANG - PLB SMPG JALAN SAHABAT | Snapped by Trees / Branches | Partly Environment | ABC Conductor | CABLE | 05-01-2021 20:42 | 05-01-2021 21:25 | 43 | 06-01-2021 12:29 | 07-01-2021 21:38 | 33 | 07-01-2021 21:50 | 49.17
Northern | K1 | TRIPPING-2021-KED-10 | 0245/20210106/010 | Kedah | Kuala Nerang | 11kV | Overhead | 06-01-2021 14:17 | PPU NAKA 3K5 | PPU NAKA 3K5 | PBT KUBANG KENYENG - PBT KUBANG BEMBAN | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | OVERHEAD LINES | 06-01-2021 14:21 | 06-01-2021 14:37 | 16 | 06-01-2021 23:33 | 08-01-2021 09:05 | 33 | 08-01-2021 10:21 | 44.07
Northern | K1 | TRIPPING-2021-PLS-4 | 2610/20210107/025 | Perlis | Perlis | 11kV | Underground | 07-01-2021 09:08 | PPU POLITEKNIK PAUH PERLIS 2 | PPU POLITEKNIK PAUH PERLIS CB2 | PPUPOLITEKNIK PAUH PERLIS CB2 - TMN DESA ULU PAUH |  |  |  | CABLE | 07-01-2021 09:14 | 07-01-2021 09:58 | 44 | 07-01-2021 22:53 | 28-01-2021 15:49 | 496 | 28-01-2021 16:22 | 511.23
Northern | K1 | TRIPPING-2021-KED-13 | 0245/20210109/029 | Kedah | Kuala Nerang | 11kV | Underground | 09-01-2021 17:20 | PPU KUALA NERANG KN3 | PPU KUALA NERANG KN3 | PBT KG. BELIMBING - PBT KG. BENDANG RAJA, - S/S FELDA BELIMBING - PBT KG. LABI |  |  |  | CABLE | 09-01-2021 17:21 | 09-01-2021 17:30 | 9 | 10-01-2021 00:05, 10-01-2021 00:07 | 11-01-2021 08:43, 10-01-2021 22:35 | 32, 22 | 11-01-2021 09:15 | 39.92
Northern | K1 | TRIPPING-2021-KED-14 | 0245/20210109/120 | Kedah | Kuala Nerang | 11kV | Underground | 09-01-2021 18:01 | PPU KUALA NERANG KN5 | PPU KUALA NERANG KN5 | PDB TMN AKASIA - PADAT LDG BUKIT NGAUN | Insulation Failed, Shorted by Water Ingress | Partly Weather | Cable Termination | OVERHEAD LINES | 09-01-2021 18:05 | 09-01-2021 18:18 | 13 | 10-01-2021 02:34 | 11-01-2021 18:40 | 40 | 11-01-2021 19:12 | 49.18
Northern | K1 | TRIPPING-2021-KED-15 | 0245/20210109/118 | Kedah | Kuala Nerang | 11kV | Overhead | 09-01-2021 19:25 | PPU KUALA NERANG KN1 | A/R TG SEBERANG |  | Failed, Shorted by Old External Damage | Partly Environment | Straight Through Joint | OTHER | 09-01-2021 19:28 | 09-01-2021 20:05 | 37 |  |  |  | 09-01-2021 20:09 | 0.73
Northern | K1 | TRIPPING-2021-KED-20 | 0245/20210111/025 | Kedah | Kuala Nerang | 11kV | Underground | 11-01-2021 11:39 | PPU KUALA NERANG KN3 | A/R KG BELIMBNG KKN00196 | PBT KG. BENDANG RAJA - S/S FELCRA KG BELIMBING | Core Opened | Partly Environment | Cable | CABLE | 11-01-2021 11:55 | 11-01-2021 11:59 | 4 | 11-01-2021 23:30 | 12-01-2021 23:27 | 23 | 14-01-2021 10:15 | 70.6
Northern | K1 | TRIPPING-2021-PLS-5 | 2610/20210116/002 | Perlis | Perlis | 11kV | Underground | 16-01-2021 07:19 | PPU SIMPANG EMPAT CB6 | PPU SIMPANG EMPAT CB6 | PDB SM SYED ALWI - TMN BUMITA | Failed, Shorted by Old External Damage | Partly Environment | Transition Joint | CABLE | 16-01-2021 07:22 | 16-01-2021 07:49 | 27 | 18-01-2021 22:25 | 05-02-2021 10:14 | 419 | 05-02-2021 10:20 | 483.02
Northern | K1 | TRIPPING-2021-KED-26 | 0242/20210116/011 | Kedah | Jitra | 11kV | Underground | 16-01-2021 12:39 | PMU TANJUNG PAUH TP15 | PDB IBUSAWAT TELEKOM JTR-TLKOM KJT00460 CB1 | PDB MADA JITRA - PDB R/AWAM JITRA | Core Opened | Partly Environment | Cable | CABLE | 16-01-2021 12:44 | 16-01-2021 13:07 | 23 | 17-01-2021 11:30 | 17-01-2021 16:52 | 5 | 17-01-2021 17:23 | 28.73
Northern | K1 | TRIPPING-2021-KED-27 | 0242/20210117/023 | Kedah | Jitra | 11kV | Underground | 17-01-2021 10:01 | PPU DARULAMAN 10K5 | PPU DARULAMAN 10K5 | PPUDARULAMAN 10K5 - PDB TMN GEMILANG (JIT) | Damaged, Soil Movement | Under Investigation | Straight Through Joint | CABLE | 17-01-2021 10:04 | 17-01-2021 10:24 | 20 | 17-01-2021 17:10 | 19-01-2021 04:48 | 35 | 19-01-2021 05:35 | 43.57
Northern | K1 | TRIPPING-2021-KED-28 | 0242/20210117/072 | Kedah | Jitra | 11kV | Underground | 17-01-2021 11:34 | PPU JERLUN SJ2 | KLG PROSES UDANG KJT01687 |  | Core Opened | Partly Environment | Cable | OTHER | 17-01-2021 12:30 | 17-01-2021 12:49 | 19 |  |  |  | 17-01-2021 14:27 | 2.88
Northern | K1 | TRIPPING-2021-PLS-6 | 2610/20210118/114 | Perlis | Perlis | 11kV | Underground | 18-01-2021 23:29 | PMU KANGAR CB16 | PVCB TMN JALI KAN02326 | MARKET KANGAR - MNR KEMAJUAN | Failed, Shorted by Old External Damage | Under Investigation | Straight Through Joint | CABLE | 18-01-2021 23:31 | 18-01-2021 23:50 | 19 | 21-01-2021 23:49 | 31-01-2021 18:16 | 234 | 31-01-2021 18:31 | 307.03
Northern | K1 | TRIPPING-2021-PLS-7 | 2610/20210122/010 | Perlis | Perlis | 11kV | Underground | 22-01-2021 10:20 | PPU MINI PPU ABI 11 | PPU MINI PPU ABI CB11 |  | Loose and Shorted | Partly Environment | Link Switch | TRANSIENT | 22-01-2021 10:50 | 22-01-2021 11:14 | 24 |  |  |  | 22-01-2021 12:00 | 1.67
Northern | K1 | TRIPPING-2021-KED-36 | 0240/20210122/052 | Kedah | Jitra | 11kV | Underground | 22-01-2021 14:33 | PPU JERLUN SJ2 | PDB KLG PROSES UDANG KERPAN KJT01687 CB1 |  | Core Opened | Defective Manufacture | Cable | TRANSIENT | 22-01-2021 14:38 | 22-01-2021 15:20 | 42 |  |  |  | 22-01-2021 16:25 | 1.87
Northern | K1 | TRIPPING-2021-PLS-8 | 2610/20210124/021 | Perlis | Perlis | 11kV | Overhead | 24-01-2021 10:13 | PPU BUKIT KETERI 5K5 | PDB RPA CHUPING 2 KAN00285 CB1 | PAT ABIM - KILANG MEDIQUIP | Damaged by Vandals | Act of Vandalism | Straight Through Joint | CABLE | 24-01-2021 10:19 | 24-01-2021 10:42 | 23 | 24-01-2021 15:21 | 27-01-2021 03:40 | 60 | 27-01-2021 04:07 | 65.9
Northern | K1 | TRIPPING-2021-PLS-9 | 2610/20210126/013 | Perlis | Perlis | 11kV | Substation | 26-01-2021 13:45 | PMU CHUPING CB7 | PDB KUBANG PERUN KAN00258 CB1 | PDB PENJARA CHUPING NO 1 - SK GUAR NANGKA | Cable Compartment - Vermin Encroachment | Partly Environment | Circuit Breaker | SWITCHGEAR | 26-01-2021 13:49 | 26-01-2021 14:21 | 32 | 28-01-2021 16:11 | 29-01-2021 04:58 | 12 | 29-01-2021 05:32 | 63.78
Northern | K1 | TRIPPING-2021-PLS-10 | 0260/20210127/015 | Perlis | Perlis | 11kV | Underground | 27-01-2021 12:44 | PMU KUALA PERLIS CB5 | PMU KUALA PERLIS CB5 | PBT KG. TELOK - KLG AIS IGLOO |  |  |  | CABLE | 27-01-2021 12:48 | 27-01-2021 13:23 | 35 | 27-01-2021 18:54 | 28-01-2021 14:39 | 19 | 29-01-2021 18:00 | 53.27
Northern | K1 | TRIPPING-2021-PLS-11 | 2610/20210128/024 | Perlis | Perlis | 11kV | Underground | 28-01-2021 12:02 | PMU KANGAR CB1 | PDB SEKOLAH VOKASIONAL KANGAR KAN00472 | SEKOLAH VOKASIONAL KANGAR - SK SRI INDRA | Failed, Shorted by Old External Damage | Under Investigation | Straight Through Joint | CABLE | 28-01-2021 12:04 | 28-01-2021 12:23 | 19 | 01-02-2021 22:26 | 03-02-2021 07:48 | 33 | 03-02-2021 08:32 | 140.5
Northern | K1 | TRIPPING-2021-PLS-12 | 2610/20210202/025 | Perlis | Perlis | 11kV | Underground | 02-02-2021 17:41 | PPU SIMPANG EMPAT CB6 | PPU SIMPANG EMPAT CB6 | SEK AGAMA AL-ISLAHIAH BOHOR - PAT BATAS LINTANG | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 02-02-2021 17:49 | 02-02-2021 18:26 | 37 | 02-02-2021 20:38, 05-02-2021 22:19, 23-02-2021 13:12 | 02-02-2021 21:18, 23-02-2021 12:25, 24-02-2021 11:35 | 0, 422, 22 | 24-02-2021 12:15 | 522.57
Northern | K1 | TRIPPING-2021-KED-70 | 0245/20210212/001 | Kedah | Kuala Nerang | 11kV | Underground | 12-02-2021 03:20 | PPU KUALA NERANG KN5 | PDB TMN SRI NERANG KKN00032 | PDB KOLEJ MARA - TAMAN MERBAU (NOP) | Failed, Shorted by Corrosive Evmnt | Under Investigation | Straight Through Joint | CABLE | 12-02-2021 03:27 | 12-02-2021 03:35 | 8 | 12-02-2021 14:50 | 13-02-2021 10:25 | 19 | 13-02-2021 10:45 | 31.42
Northern | K1 | TRIPPING-2021-PLS-13 | 2610/20210212/002 | Perlis | Perlis | 11kV | Underground | 12-02-2021 03:53 | PPU BUKIT KETERI 5K5 | PDB RPA CHUPING 2 KAN00285 CB1 | KILANG MEDIQUIP - PE MATRI | Insulation Burnt | Lack of Maintenance | Cable Termination | CABLE | 12-02-2021 04:40 | 12-02-2021 05:02 | 22 | 12-02-2021 16:05 | 13-02-2021 02:41 | 10 | 13-02-2021 03:05 | 23.2
Northern | K1 | TRIPPING-2021-KED-80 | 0240/20210215/076 | Kedah | Jitra | 11kV | Underground | 15-02-2021 15:43 | PPU KODIANG KD2 | PDB SM TUNKU BENDAHARA KJT01260 CB1 | PBT KG. TOK ARANG 1 - KG. PERING | Damaged, Shorted by Third Party Dug Up | Unavoidable Accident | Cable | CABLE | 15-02-2021 15:58 | 15-02-2021 16:32 | 34 | 15-02-2021 22:04 | 16-02-2021 13:09 | 15 | 16-02-2021 13:38 | 21.92
Northern | K1 | TRIPPING-2021-PLS-14 | 2610/20210216/076 | Perlis | Perlis | 11kV | Underground | 16-02-2021 22:06 | PMU KUALA PERLIS CB2 | VCB MAHKAMAH TINGGI PERLIS KAN00445 CB1 | MAHKAMAH TINGGI - COMP-SUB DEWAN MB-VVIP |  |  | Straight Through Joint | CABLE | 16-02-2021 22:15 | 16-02-2021 22:55 | 40 | 17-02-2021 22:48 | 01-03-2021 18:18 | 283 | 01-03-2021 18:38 | 308.53
Northern | K1 | TRIPPING-2021-PLS-15 | 2610/20210221/020 | Perlis | Perlis | 11kV | Underground | 21-02-2021 21:26 | PMU KUALA PERLIS CB5 | PMU KUALA PERLIS CB5 | KLG AIS IGLOO - PBT KG. TELOK | Failed, Shorted by Corrosive Evmnt | Under Investigation | Straight Through Joint | CABLE | 21-02-2021 21:30 | 21-02-2021 21:57 | 27 | 27-02-2021 22:54 | 16-03-2021 06:12 | 391 | 17-03-2021 10:15 | 564.82
Northern | K1 | TRIPPING-2021-PLS-16 | 2610/20210222/021 | Perlis | Perlis | 11kV | Underground | 22-02-2021 04:10 | PPU SHORUBBER CB4 | PPU SHORUBBER CB4 | PDB TMN DESA PULAI - PVCB TAMAN JALI | Failed, Shorted by Corrosive Evmnt | Under Investigation | Straight Through Joint | CABLE | 22-02-2021 04:14 | 22-02-2021 04:42 | 28 | 22-02-2021 22:39 | 29-04-2021 15:24 | 1576 | 30-04-2021 15:44 | 1619.57
Northern | K1 | TRIPPING-2021-KED-94 | 0242/20210222/010 | Kedah | Jitra | 11kV | Underground | 22-02-2021 12:24 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01798 CB1 | PBT KG. KUBANG PASU - PBT KG. JERAGAN | Damaged, Shorted by Third Party Dug Up | Under Investigation | Cable | CABLE | 22-02-2021 12:27 | 22-02-2021 12:40 | 13 | 23-02-2021 11:53 | 23-02-2021 16:21 | 4 | 23-02-2021 16:40 | 28.27
Northern | K1 | TRIPPING-2021-PLS-18 | 2610/20210302/044 | Perlis | Perlis | 11kV | Underground | 02-03-2021 21:09 | PPU SHORUBBER CB2 | VCB ALOR LANCANG KAN00834 | ALOR LANCANG - ALOR ARA TIMUR | Core Opened | Partly Environment | Cable | CABLE | 02-03-2021 21:09 | 02-03-2021 21:34 | 25 | 04-03-2021 02:13 | 18-03-2021 14:09 | 347 | 18-03-2021 14:15 | 377.1
Northern | K1 | TRIPPING-2021-PLS-19 | 2610/20210305/095 | Perlis | Perlis | 11kV | Underground | 05-03-2021 14:15 | PMU KANGAR CB16 | PMU KANGAR CB16 | TMN GUAR SYED ALWI - PVCB TMN JALI | Failed, Shorted by Corrosive Evmnt | Partly Environment | Straight Through Joint | CABLE | 05-03-2021 14:19 | 05-03-2021 14:40 | 21 | 06-03-2021 00:24, 10-03-2021 15:47 | 10-03-2021 11:15, 11-03-2021 08:20 | 106, 16 | 11-03-2021 09:09 | 138.9
Northern | K1 | TRIPPING-2021-PLS-20 | 2610/20210305/126 | Perlis | Perlis | 11kV | Underground | 05-03-2021 19:41 | PMU KUALA PERLIS CB6 | TMN SENTOSA KUALA PERLIS KAN00627 CB1 | PDB PROCESSING FACTORY | Core Opened | Defective Manufacture | Cable | OTHER | 05-03-2021 19:41 | 05-03-2021 20:11 | 30 |  |  |  | 07-03-2021 18:25 | 46.73
Northern | K1 | TRIPPING-2021-PLS-21 | 2610/20210313/003 | Perlis | Perlis | 11kV | Underground | 13-03-2021 03:01 | PPU SIMPANG EMPAT CB4 | PPU SIMPANG EMPAT CB4 | PDB KLG BERAS REMODAL - S/S KG SG BELATI | Insulation Burnt | Improper Installation | Cable Termination | CABLE | 13-03-2021 03:04 | 13-03-2021 03:40 | 36 | 13-03-2021 16:56 | 13-03-2021 20:59 | 4 | 13-03-2021 22:14 | 19.22
Northern | K1 | TRIPPING-2021-PLS-22 | 2610/20210320/029 | Perlis | Perlis | 11kV | Underground | 20-03-2021 12:58 | PPU BUKIT KETERI 7K5 | PDB TMN BESERI JAYA KAN00178 CB1 | PDB TMN BESERI MURNI-VVIP - PBT LMBH BIAK | Insulation Failed, Shorted by Water Ingress | Under Investigation | Cable | CABLE | 20-03-2021 13:04 | 20-03-2021 13:43 | 39 | 20-03-2021 23:41 | 09-04-2021 16:58 | 473 | 12-04-2021 07:55 | 546.95
Northern | K1 | TRIPPING-2021-PLS-24 | 2610/20210322/012 | Perlis | Perlis | 11kV | Underground | 22-03-2021 08:01 | PMU CHUPING CB1 | PLB KAJI CUACA KAN00790 | KAJI CUACA - PDB RPA MATA AIR | Failed, Shorted by Water Ingress | Under Investigation | Straight Through Joint | CABLE | 22-03-2021 08:19 | 22-03-2021 08:44 | 25 | 22-03-2021 22:23, 27-03-2021 11:05 | 27-03-2021 10:39, 28-03-2021 11:31 | 108, 24 | 28-03-2021 11:38 | 147.62
Northern | K1 | TRIPPING-2021-PLS-25 | 2610/20210323/003 | Perlis | Perlis | 11kV | Underground | 23-03-2021 09:43 | PPU BUKIT KETERI 7K5 | PDB TMN BESERI JAYA KAN00179 CB1 |  | Core Opened | Partly Environment | Cable | OTHER | 23-03-2021 09:44 | 23-03-2021 10:14 | 30 |  |  |  | 23-03-2021 12:57 | 3.23
Northern | K1 | TRIPPING-2021-PLS-26 | 2610/20210323/021 | Perlis | Perlis | 11kV | Underground | 23-03-2021 13:06 | PPU BUKIT KETERI 7K5 | PDB TMN BESERI JAYA KAN00179 CB1 | PDB JPS TIMAH TASOH - CHALET TIMAH TASOH | Core Opened | Partly Environment | Cable | CABLE | 23-03-2021 13:06 | 23-03-2021 13:07 | 1 | 27-03-2021 11:32 | 28-03-2021 08:47 | 21 | 28-03-2021 09:10 | 116.07
Northern | K1 | TRIPPING-2021-PLS-27 | 2610/20210323/031 | Perlis | Perlis | 11kV | Underground | 23-03-2021 17:23 | PPU LOJI AIR ARAU GIS 5K5 | PPU LOJI AIR ARAU GIS 5K5 | KOMPLEK TOK ARAU - STESEN KTMB ARAU | Damaged, Shorted by Third Party Dug Up | Unavoidable Accident | Cable | CABLE | 23-03-2021 17:26 | 23-03-2021 18:05 | 39 |  |  |  | 10-04-2021 13:24 | 428.02
Northern | K1 | TRIPPING-2021-PLS-28 | 2610/20210326/013 | Perlis | Perlis | 11kV | Underground | 26-03-2021 12:14 | PPU SIMPANG EMPAT CB5 | SEK MEN SANGLANG KAN01095 CB1 | PBT PERMATANG BONGOR - PBT PERMATANG PIANGGU | Core Broken | Act of Vandalism | Cable | CABLE | 26-03-2021 12:18 | 26-03-2021 12:53 | 35 | 28-03-2021 22:30 | 01-04-2021 08:33 | 82 | 01-04-2021 09:03 | 140.82
Northern | K1 | TRIPPING-2021-PLS-29 | RE/02610/20210328/PLS29 | Perlis | Perlis | 11kV | Underground | 28-03-2021 20:25 | PMU CHUPING CB7 | SK GUAR NANGKA KAN02604 CB1 | CUSTOMER SITE - |  |  |  | OTHER | 28-03-2021 20:25 |  | 0 | 29-03-2021 13:39 | 30-03-2021 12:58 | 23 | 30-03-2021 01:58 | 29.55
Northern | K1 | TRIPPING-2021-KED-171 | 0245/20210330/001 | Kedah | Kuala Nerang | 11kV | Underground | 30-03-2021 00:41 | PPU NAKA 6K5 | A/R KG CHANDING | PBT SG. KAP - PLB LOJI AIR NAMI |  |  |  | CABLE | 30-03-2021 01:50 | 30-03-2021 01:53 | 3 | 30-03-2021 11:58 | 31-03-2021 12:02 | 24 | 01-04-2021 11:02 | 58.35
Northern | K1 | TRIPPING-2021-KED-175 | 0242/20210401/009 | Kedah | Jitra | 11kV | Substation | 01-04-2021 09:54 | PPU DARULAMAN 3K5 | KLG MAKANAN&MINUMAN JLN B.WANG KJT18990 CB1 | STN SUIS KG. BIAK - PAT PAYA KERCUT | Insulation Burnt | Defective Manufacture | Cable Termination | CABLE | 01-04-2021 10:40 | 01-04-2021 11:04 | 24 | 01-04-2021 18:41 | 02-04-2021 01:44 | 7 | 02-04-2021 01:44 | 15.83
Northern | K1 | TRIPPING-2021-KED-178 | 0242/20210401/037 | Kedah | Jitra | 11kV | Overhead | 01-04-2021 13:29 | PPU KODIANG KD5 | PPU KODIANG KD5 | PPU KODIANG KD5 - PDB RUMAH PAM SG. PERING | Opened by Vandals | Partly Environment | ABC Conductor | OVERHEAD LINES | 01-04-2021 13:33 | 01-04-2021 13:58 | 25 | 02-04-2021 02:45 | 02-04-2021 05:10 | 2 | 02-04-2021 18:12 | 28.72
Northern | K1 | TRIPPING-2021-KED-179 | 0242/20210401/141 | Kedah | Jitra | 11kV | Underground | 01-04-2021 16:25 | PPU LOJI AIR ARAU GIS 12K5 | PDB SM SAINS KUBANG PASU KJT1585 CB1 |  | Bitten by Animal |  | ABC Conductor | TRANSIENT | 01-04-2021 16:30 | 01-04-2021 16:59 | 29 |  |  |  | 01-04-2021 18:01 | 1.6
Northern | K1 | TRIPPING-2021-KED-185 | 0242/20210405/055 | Kedah | Jitra | 11kV | Overhead | 05-04-2021 19:28 | PPU DARULAMAN 10K5 | PPU DARULAMAN 10K5 | MUTIARA RESIDENT NO 1 - MUTIARA RESIDENT NO 2 | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 05-04-2021 19:30 | 05-04-2021 19:38 | 8 | 05-04-2021 22:25, 06-04-2021 00:57 | 06-04-2021 00:52, 06-04-2021 16:22 | 2, 15 | 06-04-2021 16:32 | 21.07
Northern | K1 | TRIPPING-2021-KED-186 | 0242/20210407/059 | Kedah | Jitra | 11kV | Underground | 07-04-2021 14:00 | PPU JERLUN SJ2 | KLG PROSES UDANG KJT01687 | KUALA KERPAN KECIL - KUALA SANGLANG 2 | Core Broken | Act of Vandalism | Cable | CABLE | 07-04-2021 14:00 | 07-04-2021 14:40 | 40 | 08-04-2021 10:40 | 09-04-2021 20:23 | 33 | 09-04-2021 20:35 | 54.58
Northern | K1 | TRIPPING-2021-PLS-31 | 2610/20210410/043 | Perlis | Perlis | 11kV | Underground | 10-04-2021 17:45 | PPU SIMPANG EMPAT CB5 | SEK MEN SANGLANG KAN01095 CB1 | PBT PERMATANG PIANGGU - PADANG KERIA | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 10-04-2021 17:46 | 10-04-2021 18:20 | 34 | 11-04-2021 22:14 | 12-04-2021 04:02 | 5 | 12-04-2021 04:15 | 34.5
Northern | K1 | TRIPPING-2021-PLS-33 | 2610/20210413/059 | Perlis | Perlis | 11kV | Underground | 13-04-2021 18:19 | PMU KANGAR CB2 | PDB TELEKOM LAMA KANGAR KAN00550 CB1 | C/SUB SK SRI PERLIS - PBT BUKIT KAYA | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 13-04-2021 18:21 | 13-04-2021 18:45 | 24 | 13-04-2021 23:29 | 14-04-2021 04:37 | 5 | 14-04-2021 04:47 | 10.47
Northern | K1 | TRIPPING-2021-KED-195 | 0242/20210414/016 | Kedah | Jitra | 11kV | Underground | 14-04-2021 04:29 | PPU PELUBANG PL3 | PDB SK PENGHULU HJ DARUS KJT00700 CB1 |  | Dielectric breakdown | Dielectric Deterioration | Cable Termination | OTHER | 14-04-2021 04:32 | 14-04-2021 05:12 | 40 |  |  |  | 14-04-2021 05:46 | 1.28
Northern | K1 | TRIPPING-2021-KED-200 | 0242/20210415/130 | Kedah | Jitra | 11kV | Underground | 15-04-2021 14:35 | PPU LOJI AIR ARAU GIS 12K5 | LPAU 12K5 | KLG BERAS UTARA SEED - S/S LAHAR KEMELING (NOP) | Insulation Failed, Shorted by Water Ingress | Under Investigation | Cable | CABLE | 15-04-2021 14:38 | 15-04-2021 15:20 | 42 | 16-04-2021 11:25 | 16-04-2021 18:47 | 7 | 16-04-2021 19:15 | 28.67
Northern | K1 | TRIPPING-2021-KED-204 | 0242/20210417/070 | Kedah | Jitra | 11kV | Underground | 17-04-2021 18:32 | PPU UUM SINTOK ST5 | PPU UUM SINTOK ST5 | PPU UUM SINTOK ST5 - PLB RUMAH PAM MARDI | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 17-04-2021 18:34 | 17-04-2021 19:17 | 43 | 18-04-2021 01:21 | 18-04-2021 04:16 | 2 | 18-04-2021 04:26 | 9.9
Northern | K1 | TRIPPING-2021-PLS-34 | 2610/20210421/003 | Perlis | Perlis | 11kV | Substation | 21-04-2021 06:58 | PPU SHORUBBER CB3 | PDB MIEL KUKUM JEJAWI KAN00733 CB1 | PAT KEPALA 10 LONG BOH | Loose and Shorted | Partly Environment | Link Switch | OTHER | 21-04-2021 07:03 | 21-04-2021 07:37 | 34 |  |  |  | 21-04-2021 07:52 | 0.9
Northern | K1 | TRIPPING-2021-PLS-35 | 2610/20210422/021 | Perlis | Perlis | 11kV | Underground | 22-04-2021 08:10 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 | PDB RPA JEJAWI - PDT KUKUM JEJAWI | Core Opened | Partly Environment | Cable | CABLE | 22-04-2021 08:13 | 22-04-2021 08:35 | 22 | 25-04-2021 23:10 | 09-05-2021 02:35 | 315 | 09-05-2021 02:45 | 402.58
Northern | K1 | TRIPPING-2021-PLS-36 | 2610/20210424/055 | Perlis | Perlis | 11kV | Underground | 24-04-2021 14:48 | PMU KUALA PERLIS CB5 | KOMPLEK DUN PERLIS KAN00592 CB1 | TMN BUMITA KAN00593 | Cable Compartment - Vermin Encroachment | Partly Environment | Circuit Breaker | SWITCHGEAR | 24-04-2021 14:52 | 24-04-2021 15:14 | 22 | 24-04-2021 17:39, 02-05-2021 08:35 | 02-05-2021 06:33, 02-05-2021 17:29 | 180, 8 | 02-05-2021 23:19 | 200.52
Northern | K1 | TRIPPING-2021-PLS-39 | RE/2610/20210502/PLS/01 | Perlis | Perlis | 11kV | Underground | 02-05-2021 06:57 | PMU CHUPING CB7 | PDB TMN SRI PUTERI KAN02782 |  |  |  |  | OTHER | 02-05-2021 07:05 | 02-05-2021 07:40 | 35 | 02-05-2021 09:11 | 02-05-2021 17:30 | 8 | 02-05-2021 17:00 | 10.05
Northern | K1 | TRIPPING-2021-KED-254 | 0245/20210510/062 | Kedah | Kuala Nerang | 11kV | Underground | 10-05-2021 12:32 | PPU KUALA NERANG KN2 | A/R SEK MEN PEDU | PLB KG. TANJUNG LUAR - PBT PADANG SETUL | Insulation Failed, Shorted by Old External Damage | Partly Environment | Cable | CABLE | 10-05-2021 12:35 | 10-05-2021 12:58 | 23 | 10-05-2021 18:49 | 12-05-2021 09:54 | 39 | 12-05-2021 10:45 | 46.22
Northern | K1 | TRIPPING-2021-PLS-41 | 2610/20210515/001 | Perlis | Perlis | 11kV | Underground | 15-05-2021 21:15 | PMU CHUPING CB7 | SK GUAR NANGKA KAN02604 | RE HBH GLOBAL |  |  |  | OTHER | 15-05-2021 21:16 | 15-05-2021 21:30 | 14 | 15-05-2021 22:12 | 16-05-2021 18:55 | 20 | 16-05-2021 18:04 | 20.82
Northern | K1 | TRIPPING-2021-KED-269 | 0242/20210518/002 | Kedah | Jitra | 11kV | Underground | 18-05-2021 01:36 | PPU JERLUN SJ1 | PPU JERLUN SJ1 |  | Dielectric breakdown | Dielectric Deterioration | Cable Termination | OTHER | 18-05-2021 01:38 | 18-05-2021 02:20 | 42 |  |  |  | 18-05-2021 03:22 | 1.77
Northern | K1 | TRIPPING-2021-PLS-42 | 2610/20210519/099 | Perlis | Perlis | 11kV | Underground | 19-05-2021 19:16 | PMU KUALA PERLIS CB2 | PMU KUALA PERLIS CB2 | PMUKUALA PERLIS CB2 - TMN BUNGA PADI | Snapped by Trees / Branches | Partly Environment | ABC Conductor | CABLE | 19-05-2021 19:23 | 19-05-2021 19:30 | 7 | 20-05-2021 00:20 | 21-05-2021 02:57 | 26 | 21-05-2021 04:07 | 32.85
Northern | K1 | TRIPPING-2021-PLS-43 | 2610/20210520/031 | Perlis | Perlis | 11kV | Underground | 20-05-2021 21:06 | PMU KUALA PERLIS CB6 | TMN SENTOSA KUALA PERLIS KAN00627 CB1 | PDB PROCESSING FACTORY - PDB AMAN FISHMEAL | Insulation Failed, Shorted by Water Ingress | Under Investigation | Cable | CABLE | 20-05-2021 21:09 | 20-05-2021 21:27 | 18 | 24-05-2021 22:18 | 08-06-2021 15:42 | 353 | 08-06-2021 16:10 | 451.07
Northern | K1 | TRIPPING-2021-PLS-44 | 2610/20210522/018 | Perlis | Perlis | 11kV | Underground | 22-05-2021 09:21 | PPU BUKIT KETERI 5K5 | PPU BUKIT KETERI 5K5 | PDB RPA CHUPING 2 - PAT PAYA KELUBI | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 22-05-2021 09:32 | 22-05-2021 10:05 | 33 | 22-05-2021 10:44 | 23-05-2021 01:17 | 14 | 23-05-2021 01:17 | 15.93
Northern | K1 | TRIPPING-2021-KED-278 | 0242/20210524/003 | Kedah | Jitra | 11kV | Underground | 24-05-2021 04:08 | PMU TANJUNG PAUH TP6 | BELLEZA GARDEN HOMES KJT18927 CB1 | PDB SK BKT TINGGI - LEBUHRAYA KEPALA BATAS | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 24-05-2021 04:26 | 24-05-2021 05:10 | 44 | 24-05-2021 13:33 | 24-05-2021 18:10 | 4 | 24-05-2021 18:30 | 14.37
Northern | K1 | TRIPPING-2021-KED-279 | 0242/20210524/105 | Kedah | Jitra | 11kV | Underground | 24-05-2021 12:16 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01797 CB1 | S/S BLOK VALVE M2 - PAT KG. WANG PERAH | Damaged, Shorted by Third Party Dug Up | Improper Laying | Cable | CABLE | 24-05-2021 12:19 | 24-05-2021 12:50 | 31 | 24-05-2021 13:18 | 25-05-2021 09:53 | 20 | 25-05-2021 09:53 | 21.62
Northern | K1 | TRIPPING-2021-KED-284 | 0242/20210527/001 | Kedah | Jitra | 11kV | Overhead | 27-05-2021 04:33 | PPU KODIANG KD1 | PPU KODIANG KD1 | PAT PPRT KG. WANG | Insulation Breakdown | Animal | Cable Termination | CABLE | 27-05-2021 04:36 | 27-05-2021 05:10 | 34 |  |  |  | 27-05-2021 06:15 | 1.7
Northern | K1 | TRIPPING-2021-PLS-48 | 2610/20210529/001 | Perlis | Perlis | 11kV | Underground | 29-05-2021 02:52 | PMU KANGAR CB5 | PVCB REPOH CERIA-VVIP KAN02632 CB1 | PAT KG. TANJUNG - PLB JALAN SANTAN | Core Opened | Partly Environment | Cable | CABLE | 29-05-2021 02:55 | 29-05-2021 03:24 | 29 | 31-05-2021 21:52 | 11-08-2021 12:06 | 1718 | 11-08-2021 12:19 | 1785.45
Northern | K1 | TRIPPING-2021-KED-292 | 0245/20210530/023 | Kedah | Kuala Nerang | 11kV | Underground | 30-05-2021 10:39 | PPU KUALA NERANG KN3 | PPU KUALA NERANG KN3 | SAT BUKIT NYAMUK - PBT BUKIT NYAMUK, - PDB R/AWAM KUALA NERANG - PBT KG. BELIMBING | Damaged, Shorted by Third Party Dug Up | Improper Route | Cable | CABLE, CABLE | 30-05-2021 10:42 | 30-05-2021 11:03 | 21 | 30-05-2021 14:20, 30-05-2021 14:23 | 31-05-2021 09:41, 05-06-2021 10:45 | 19, 140 | 05-06-2021 13:51 | 147.2
Northern | K1 | TRIPPING-2021-KED-297 | 0242/20210601/004 | Kedah | Jitra | 11kV | Underground | 01-06-2021 08:47 | PPU UUM SINTOK ST6 | PDB ASRAMA UUM KJT01743 | ASRAMA UUM - SS BUKIT DAMAR | Dielectric breakdown | Improper Installation | Cable Termination | CABLE | 01-06-2021 08:48 | 01-06-2021 09:23 | 35 | 01-06-2021 16:29 | 02-06-2021 00:56 | 8 | 02-06-2021 01:10 | 16.38
Northern | K1 | TRIPPING-2021-PLS-49 | 2610/20210602/026 | Perlis | Perlis | 11kV | Underground | 02-06-2021 17:29 | PPU BUKIT KETERI 7K5 | PDB TMN BESERI JAYA KAN00179 CB1 | PDB JPS TIMAH TASOH - CHALET TIMAH TASOH | Damaged, Shorted by Third Party Dug Up | Unavoidable Accident | Cable | CABLE | 02-06-2021 17:34 | 02-06-2021 18:00 | 26 | 05-06-2021 11:02 | 06-06-2021 04:10 | 17 | 06-06-2021 04:35 | 83.1
Northern | K1 | TRIPPING-2021-PLS-50 | 2610/20210604/030 | Perlis | Perlis | 11kV | Underground | 04-06-2021 16:36 | PPU BUKIT KETERI 7K5 | PPU BUKIT KETERI 7K5 | PPU BUKIT KETERI 7K5 - PDB TMN BESERI JAYA | Failed, Shorted by Old External Damage | Under Investigation | Transition Joint | CABLE | 04-06-2021 16:47 | 04-06-2021 17:24 | 37 | 08-06-2021 22:11 | 16-06-2021 09:51 | 179 | 16-06-2021 10:21 | 281.75
Northern | K1 | TRIPPING-2021-PLS-51 | 2610/20210605/083 | Perlis | Perlis | 11kV | Overhead | 05-06-2021 18:25 | PPU SHORUBBER CB6 | PPU SHORUBBER CB6 | PPU SHORUBBER CB6 - PDB POLIKLINIK ARAU | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 05-06-2021 18:27 | 05-06-2021 18:56 | 29 | 05-06-2021 19:22, 12-06-2021 10:45 | 08-06-2021 00:29, 15-06-2021 15:53 | 53, 77 | 16-06-2021 21:11 | 266.77
Northern | K1 | TRIPPING-2021-KED-308 | 0242/20210606/003 | Kedah | Jitra | 11kV | Underground | 06-06-2021 06:46 | PPU DARULAMAN 4K5 | RUMAH KEDAI 50 UNIT KJT19306 | RUMAH KEDAI 50 UNIT KJT19306 | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 06-06-2021 06:51 |  | 0 | 06-06-2021 08:20, 06-06-2021 19:14 | 06-06-2021 11:49, 06-06-2021 23:24 | 3, 4 | 06-06-2021 23:30 | 16.73
Northern | K1 | TRIPPING-2021-KED-313 | 0245/20210609/021 | Kedah | Kuala Nerang | 11kV | Underground | 09-06-2021 22:24 | PPU NAKA 6K5 | AR CHANDING KKN00426 | A/R KG CHANDING - KEDA KG BAGAN | Failed, Shorted by Old External Damage | Partly Environment | Transition Joint | CABLE | 09-06-2021 22:26 | 09-06-2021 23:00 | 34 | 10-06-2021 00:34 | 11-06-2021 02:40 | 26 | 11-06-2021 03:20 | 28.93
Northern | K1 | TRIPPING-2021-PLS-52 | 2610/20210611/004 | Perlis | Perlis | 11kV | Underground | 11-06-2021 08:18 | PPU MINI PPU ABI 11 | PPU MINI PPU ABI CB11 | PLB SMPG KURUNG BATANG - PAT SMPG SG SIRAN | Cracked | Partly Environment | Drop Out Fuse | CABLE | 11-06-2021 09:16 | 11-06-2021 09:23 | 7 |  |  |  | 11-06-2021 12:26 | 4.13
Northern | K1 | TRIPPING-2021-PLS-53 | 2610/20210612/020 | Perlis | Perlis | 11kV | Underground | 12-06-2021 18:29 | PPU SIMPANG EMPAT CB9 | PPU SIMPANG EMPAT CB9 | PBT BANIR TEMBUS - PDB PKNPS SMPG EMPAT | Failed, Shorted by Corrosive Evmnt | Under Investigation | Straight Through Joint | CABLE | 12-06-2021 18:35 | 12-06-2021 19:03 | 28 | 13-06-2021 22:13 | 30-06-2021 07:07 | 392 | 30-06-2021 07:09 | 420.67
Northern | K1 | TRIPPING-2021-PLS-54 | 2610/20210613/017 | Perlis | Perlis | 11kV | Underground | 13-06-2021 15:30 | PMU KUALA PERLIS CB6 | PDB AMAN FISHMEAL KAN00623 CB1 | SMK SERIAB - PLB BEHOR TEMAK | Damaged, Shorted by Third Party Dug Up | Improper Laying | Cable | CABLE | 13-06-2021 16:16 | 13-06-2021 16:18 | 2 | 17-06-2021 21:58 | 27-06-2021 17:43 | 235 | 27-06-2021 17:51 | 338.35
Northern | K1 | TRIPPING-2021-PLS-55 | 2610/20210614/017 | Perlis | Perlis | 11kV | Underground | 14-06-2021 11:44 | PPU BUKIT KETERI 9K5 | PPU BUKIT KETERI 9K5 | PPU BUKIT KETERI 9K5 - RPA MATA AIR | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 14-06-2021 11:47 | 14-06-2021 12:07 | 20 | 15-06-2021 21:56 | 21-06-2021 04:13 | 126 | 21-06-2021 04:41 | 160.95
Northern | K1 | TRIPPING-2021-PLS-56 | 2610/20210620/001 | Perlis | Perlis | 11kV | Underground | 20-06-2021 00:00 | PPU PADANG BESAR CB2 | PEKAN SAYUR PEKAN KAKI BUKIT KAN00131 | PDB BDR BARU WANG KELIAN - PDB PEKAN KAKI BUKIT | Insulation Breakdown | Insulation Deterioration | Conductor | OVERHEAD LINES | 20-06-2021 00:01 | 20-06-2021 00:10 | 9 | 20-06-2021 17:19 | 20-06-2021 23:34 | 6 | 21-06-2021 00:54 | 24.9
Northern | K1 | TRIPPING-2021-KED-342 | 0242/20210624/023 | Kedah | Jitra | 11kV | Overhead | 25-06-2021 00:03 | PMU TANJUNG PAUH TP20 | TMN PELANGI KJT01863 |  |  |  | ABC Conductor | TRANSIENT | 25-06-2021 00:12 | 25-06-2021 00:33 | 21 |  |  |  | 25-06-2021 01:06 | 1.05
Northern | K1 | TRIPPING-2021-PLS-57 | 2610/20210626/008 | Perlis | Perlis | 11kV | Underground | 26-06-2021 15:31 | PPU BUKIT KETERI 7K5 | PDB TMN BESERI JAYA KAN00179 CB1 | PLB JALAN LENCONGAN - CCRC BKT CHABANG | Damaged, Shorted by Third Party Dug Up | Act of Vandalism | Cable | CABLE | 26-06-2021 15:32 | 26-06-2021 16:12 | 40 | 28-06-2021 10:24 | 08-09-2021 04:42 | 1722 | 08-09-2021 04:56 | 1765.42
Northern | K1 | TRIPPING-2021-PLS-58 | RE/2610/20210628/PLS-58 | Perlis | Perlis | 11kV | Underground | 28-06-2021 19:35 | PMU KUALA PERLIS CB13 | KPLS CB13 |  |  |  |  | OTHER | 28-06-2021 19:45 | 28-06-2021 20:25 | 40 | 28-06-2021 21:25 | 28-06-2021 22:49 | 1 | 28-06-2021 10:48 | -8.78
Northern | K1 | TRIPPING-2021-PLS-59 | 2610/20210630/005 | Perlis | Perlis | 11kV | Underground | 30-06-2021 07:49 | PPU SIMPANG EMPAT CB9 | PPU SIMPANG EMPAT CB9 | PKNPS SIMPANG 4 - BANIR TEMBUS | Failed, Shorted by Corrosive Evmnt | Partly Environment | Transition Joint | CABLE | 30-06-2021 07:52 | 30-06-2021 07:58 | 6 | 30-06-2021 08:14 | 09-07-2021 11:27 | 219 | 11-07-2021 10:30 | 266.68
Northern | K1 | TRIPPING-2021-PLS-60 | 2610/20210701/005 | Perlis | Perlis | 11kV | Underground | 01-07-2021 05:01 | PPU MINI PPU ABI 11 | PPU MINI PPU ABI CB11 | PAT SMPG SG SIRAN | Damaged by Animal | Partly Environment | Drop Out Fuse | TRANSIENT | 01-07-2021 05:47 | 01-07-2021 06:07 | 20 |  |  |  | 01-07-2021 06:22 | 1.35
Northern | K1 | TRIPPING-2021-PLS-61 | 2610/20210701/027 | Perlis | Perlis | 11kV | Underground | 01-07-2021 07:56 | PPU BUKIT KETERI 7K5 | PPU BUKIT KETERI 7K5 | PPU BUKIT KETERI 7K5 - PDB TMN BESERI JAYA | Insulation Breakdown | Insulation Deterioration | Conductor | OVERHEAD LINES | 01-07-2021 08:04 | 01-07-2021 08:05 | 1 | 01-07-2021 21:28 | 03-07-2021 00:17 | 26 | 03-07-2021 10:57 | 51.02
Northern | K1 | TRIPPING-2021-PLS-62 | 2610/20210702/120 | Perlis | Perlis | 11kV | Underground | 02-07-2021 19:23 | PPU BUKIT KETERI 5K5 | PPU BUKIT KETERI 5K5 | PLB PMU BUKIT KETERI (L) - PDB RPA CHUPING 2 | Damaged, Shorted by Third Party Dug Up | Unavoidable Accident | Cable | CABLE | 02-07-2021 19:24 | 02-07-2021 19:32 | 8 | 03-07-2021 22:22, 06-07-2021 00:21 | 05-07-2021 23:10, 14-07-2021 22:19 | 48, 213 | 14-07-2021 22:45 | 291.37
Northern | K1 | TRIPPING-2021-PLS-63 | 2610/20210703/002 | Perlis | Perlis | 11kV | Underground | 03-07-2021 02:30 | PMU CHUPING CB5 | PMU CHUPING CB5 | PMU CHUPING CB5 - RKTRI 11K5 | Core Opened | Partly Environment | Cable | CABLE |  |  | 0 | 04-07-2021 00:18 | 10-08-2021 13:57 | 901 | 10-08-2021 13:57 | 923.45
Northern | K1 | TRIPPING-2021-PLS-64 | 2610/20210703/041 | Perlis | Perlis | 11kV | Underground | 03-07-2021 23:05 | PMU KANGAR CB5 | PVCB REPOH CERIA-VVIP KAN02632 CB1 |  | Shorted by Animal | Partly Environment | Jumper to Drop Out Fuse Wire | TRANSIENT | 03-07-2021 23:07 | 03-07-2021 23:27 | 20 |  |  |  | 04-07-2021 00:06 | 1.02
Northern | K1 | TRIPPING-2021-PLS-65 | 2610/20210705/008 | Perlis | Perlis | 11kV | Substation | 05-07-2021 06:51 | PPU PADANG BESAR CB2 | PPU PADANG BESAR CB2 | PPU PADANG BESAR CB2 - FISHING NET | Cable Compartment - Vermin Encroachment | Partly Environment | Circuit Breaker | CABLE | 05-07-2021 07:00 | 05-07-2021 07:04 | 4 | 05-07-2021 16:57 | 05-07-2021 19:16 | 2 | 05-07-2021 19:32 | 12.68
Northern | K1 | TRIPPING-2021-PLS-66 | 2610/20210711/019 | Perlis | Perlis | 11kV | Underground | 11-07-2021 17:45 | PMU KANGAR CB12 | PMU KANGAR CB12 | PVCB TMN MERPATI - PDB DRAGON & PHEONIX 2 | Core Opened | Defective Manufacture | Cable | CABLE | 11-07-2021 17:49 | 11-07-2021 18:10 | 21 | 13-07-2021 00:46 | 25-07-2021 16:46 | 304 | 26-07-2021 18:14 | 360.48
Northern | K1 | TRIPPING-2021-PLS-67 | 2610/20210711/015 | Perlis | Perlis | 11kV | Underground | 11-07-2021 17:45 | PMU KANGAR CB10 | PMU KANGAR CB10 | PMU KANGAR CB10 - PDB FLAT POLIS KANGAR | Core Opened | Defective Manufacture | Cable | CABLE | 11-07-2021 17:49 | 11-07-2021 18:15 | 26 |  |  |  | 11-07-2021 21:28 | 3.72
Northern | K1 | TRIPPING-2021-PLS-68 | 2610/20210711/294 | Perlis | Perlis | 11kV | Underground | 11-07-2021 19:44 | PMU KANGAR CB9 | PDB MEDAN KANGAR 2 KAN00529 CB1 | MEDAN KANGAR2 - MEDAN KANGAR 1, - PDB KOMP AGAMA ISLAM - PDB PEJABAT LHDN | Core Opened | Defective Manufacture | Cable | CABLE, CABLE | 11-07-2021 19:55 | 11-07-2021 20:25 | 30 | 12-07-2021 21:44, 12-07-2021 23:35, 21-09-2021 00:00 | 12-07-2021 23:29, 16-07-2021 04:27, 26-09-2021 10:40 | 1, 76, 130 | 26-09-2021 11:05 | 1839.35
Northern | K1 | TRIPPING-2021-PLS-69 | 2610/20210712/021 | Perlis | Perlis | 11kV | Underground | 12-07-2021 15:27 | PPU MINI PPU ABI CB13 | MINI PPU ABI CB13 | GOLF PUTRA - KUARI BATU SYED OMAR 1 | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 12-07-2021 16:10 | 12-07-2021 16:14 | 4 | 13-07-2021 10:43 | 13-07-2021 17:21 | 6 | 13-07-2021 17:44 | 26.28
Northern | K1 | TRIPPING-2021-KED-383 | 0242/20210714/042 | Kedah | Jitra | 11kV | Underground | 14-07-2021 20:39 | PPU CHANGLOON CL3 | PPU CHANGLOON CL3 | PLD FELDA BATU 8 CHANGLUN - R/PAM JLN KODIANG | Failed, Shorted by Old External Damage | Under Investigation | Straight Through Joint | CABLE | 14-07-2021 20:41 | 14-07-2021 21:10 | 29 | 15-07-2021 10:08 | 15-07-2021 18:19 | 8 | 15-07-2021 18:37 | 21.97
Northern | K1 | TRIPPING-2021-PLS-70 | 2610/20210717/005 | Perlis | Perlis | 11kV | Underground | 17-07-2021 09:22 | PPU PADANG BESAR CB2 | VCB PEKAN KAKI BUKIT KAN00140 |  | Mechanical | Trip circuit failure | RMU SF6 | OTHER | 17-07-2021 09:23 | 17-07-2021 10:05 | 42 |  |  |  | 17-07-2021 12:55 | 3.55
Northern | K1 | TRIPPING-2021-KED-388 | 0245/20210718/012 | Kedah | Kuala Nerang | 11kV | Underground | 18-07-2021 09:17 | PPU PEDU KKN00798 | PPU PEDU KKN00798 | KG TONG PELU - PLB KG. TANJUNG LUAR | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 18-07-2021 09:18 | 18-07-2021 09:48 | 30 | 18-07-2021 19:59 | 20-07-2021 01:28 | 29 | 20-07-2021 02:20 | 41.05
Northern | K1 | TRIPPING-2021-PLS-71 | RE/2610/20210724/001 | Perlis | Perlis | 11kV | Underground | 24-07-2021 17:43 | PMU CHUPING CB7 | TMN SRI PUTERI KAN02782 |  |  |  |  | OTHER | 24-07-2021 17:50 |  | 0 | 24-07-2021 18:49 | 25-07-2021 09:32 | 14 | 25-07-2021 09:32 | 15.82
Northern | K1 | TRIPPING-2021-KED-401 | 0245/20210726/004 | Kedah | Kuala Nerang | 11kV | Underground | 26-07-2021 11:30 | PPU KUALA NERANG KN4 | PDB SMK KUALA NERANG KKN00054 CB1 | PBT PONG MANIS - TANDOP BESAR | Damaged, Shorted by Third Party Dug Up | Unavoidable Accident | Cable | CABLE | 26-07-2021 11:32 | 26-07-2021 11:40 | 8 | 26-07-2021 14:01 | 28-07-2021 10:47 | 44 | 28-07-2021 12:10 | 48.67
Northern | K1 | TRIPPING-2021-KED-412 | 0412/20210730/033 | Kedah | Jitra | 11kV | Substation | 30-07-2021 20:32 | PPU PELUBANG PL2 | PPU PELUBANG PL2 | PPUPELUBANG PL2 | Damaged | Partly Environment | Transformer | TRANSFORMER | 30-07-2021 20:35 | 30-07-2021 21:09 | 34 | 30-07-2021 21:10, 31-07-2021 10:57 | 30-07-2021 23:17, 02-08-2021 01:50 | 2, 38 | 02-08-2021 01:50 | 53.3
Northern | K1 | TRIPPING-2021-PLS-72 | 2610/20210730/042 | Perlis | Perlis | 11kV | Underground | 30-07-2021 22:22 | PPU SIMPANG EMPAT CB1 | PDB KLG PADI MAJU KAN01040 CB1 |  |  |  |  | TRANSIENT | 30-07-2021 22:24 | 30-07-2021 22:42 | 18 |  |  |  | 30-07-2021 23:20 | 0.97
Northern | K1 | TRIPPING-2021-PLS-73 | 2610/20210731/023 | Perlis | Perlis | 11kV | Underground | 01-08-2021 00:35 | PMU KANGAR CB2 | PDB TELEKOM LAMA KANGAR KAN00551 CB1 | PDB TMN JAYADIRI - PDB TMN MUTIARA 3 | Core Opened | Defective Manufacture | Cable | CABLE | 01-08-2021 00:36 | 01-08-2021 01:14 | 38 | 01-08-2021 21:47 | 17-08-2021 03:06 | 365 | 17-08-2021 03:19 | 386.73
Northern | K1 | TRIPPING-2021-KED-418 | 0242/20210802/001 | Kedah | Jitra | 11kV | Overhead | 02-08-2021 00:11 | PPU JERLUN SJ2 | PDB KLG PROSES UDANG KERPAN KJT01687 CB1 |  | Insulation Failed and Shorted | Partly Environment | Cable Termination | OTHER | 02-08-2021 00:16 | 02-08-2021 01:10 | 54 |  |  |  | 02-08-2021 02:41 | 2.5
Northern | K1 | TRIPPING-2021-PLS-74 | RE/2610/20210811/PLS-74 | Perlis | Perlis | 11kV | Underground | 11-08-2021 16:45 | PMU CHUPING CB7 | SK GUAR NANGKA KAN02604 | RE HBH GLOBAL |  |  |  | OTHER | 11-08-2021 16:47 |  | 0 |  |  |  | 14-08-2021 13:25 | 68.67
Northern | K1 | TRIPPING-2021-PLS-75 | 2610/20210812/019 | Perlis | Perlis | 11kV | Underground | 12-08-2021 18:45 | PMU KANGAR CB13 | PVCB SHOERUBBER KAN00740 CB1 | PVCB SHOERUBBER - PDB SHOERUBBER LAMA | Insulation Burnt | Partly Environment | Cable Termination | CABLE | 12-08-2021 18:46 | 12-08-2021 19:15 | 29 | 13-08-2021 15:30 | 13-08-2021 15:54 | 0 | 13-08-2021 16:10 | 21.42
Northern | K1 | TRIPPING-2021-KED-446 | 0245/20210816/009 | Kedah | Kuala Nerang | 11kV | Underground | 16-08-2021 15:31 | PPU KUALA NERANG KN2 | A/R SEK MEN PEDU | KG BUNGA - R/P BKT SENA |  |  |  | CABLE | 16-08-2021 15:34 | 16-08-2021 15:50 | 16 | 16-08-2021 20:29 | 17-08-2021 22:23 | 25 | 17-08-2021 22:55 | 31.4
Northern | K1 | TRIPPING-2021-KED-448 | 0242/20210817/001 | Kedah | Jitra | 11kV | Underground | 17-08-2021 01:10 | PPU JERLUN SJ2 | PDB KLG PROSES UDANG KERPAN KJT01687 CB1 | SS SAMAK RMU - | Dielectric breakdown | Dielectric Deterioration | Cable Termination | OTHER | 17-08-2021 01:14 | 17-08-2021 01:51 | 37 |  |  |  | 17-08-2021 03:10 | 2
Northern | K1 | TRIPPING-2021-PLS-76 | 2610/20210819/009 | Perlis | Perlis | 11kV | Underground | 19-08-2021 04:24 | PPU SIMPANG EMPAT CB1 | PDB KLG PADI MAJU KAN01041 CB1 | PAT PADANG PETANI - KILANG BERAS KUDUNG | Failed, Shorted by Old External Damage | Under Investigation | Straight Through Joint | OTHER | 19-08-2021 04:25 | 19-08-2021 04:55 | 30 | 19-08-2021 22:09, 19-08-2021 23:29 | 19-08-2021 22:28, 27-08-2021 08:23 | 0, 176 | 27-08-2021 09:03 | 196.65
Northern | K1 | TRIPPING-2021-PLS-77 | 2610/20210822/011 | Perlis | Perlis | 11kV | Underground | 22-08-2021 00:11 | PPU PADANG BESAR CB7 | PDB KOMP KASTAM & IMIGRESEN KAN00023 CB1 | KOMPLEK IMIGRATION & KASTAM - PDB STESEN BAS PADANG BESAR | Failed, Shorted by Old External Damage | Under Investigation | Straight Through Joint | CABLE | 22-08-2021 00:20 | 22-08-2021 01:01 | 41 | 23-08-2021 16:35 | 30-08-2021 11:03 | 162 | 31-08-2021 09:34 | 225.38
Northern | K1 | TRIPPING-2021-PLS-78 | 2610/20210824/035 | Perlis | Perlis | 11kV | Underground | 24-08-2021 20:29 | PPU SHORUBBER CB3 | PDB MIEL KUKUM JEJAWI KAN00733 CB1 | PLB CHE OK - PAT KEPALA 10 LONG BOH | Core Opened | Partly Environment | Cable | CABLE | 24-08-2021 20:30 | 24-08-2021 20:55 | 25 | 25-08-2021 17:31 | 19-09-2021 10:41 | 593 | 19-09-2021 10:55 | 614.43
Northern | K1 | TRIPPING-2021-PLS-79 | 2610/20210827/009 | Perlis | Perlis | 11kV | Underground | 27-08-2021 13:07 | PMU CHUPING CB4 | PDB TMN DESA PAUH KAN00923 CB1 | PDB TMN DESA PAUH - PDB RPA PEKAN PAUH | Insulation Failed, Shorted by Old External Damage | Partly Environment | Cable Termination | CABLE | 27-08-2021 13:09 | 27-08-2021 13:39 | 30 | 30-08-2021 19:57 | 31-08-2021 08:37 | 12 | 31-08-2021 08:49 | 91.7
Northern | K1 | TRIPPING-2021-PLS-81 | 2610/20210828/028 | Perlis | Perlis | 11kV | Underground | 28-08-2021 17:36 | PPU POLITEKNIK PAUH PERLIS 2 | PPU POLITEKNIK PAUH PERLIS CB2 | TMN KURUNG INAI - MRSM ULU PAUH | Dielectric breakdown | Dielectric Deterioration | Straight Through Joint | CABLE | 28-08-2021 17:39 | 28-08-2021 18:02 | 23 | 01-09-2021 16:59, 01-09-2021 17:01 | 01-09-2021 16:59, 04-09-2021 07:24 | 0, 62 | 04-09-2021 07:45 | 158.15
Northern | K1 | TRIPPING-2021-KED-471 | 0242/20210829/022 | Kedah | Jitra | 11kV | Underground | 29-08-2021 16:42 | PPU UUM SINTOK ST5 | PPU UUM SINTOK ST5 |  | Dielectric breakdown | Dielectric Deterioration | Cable Termination | OTHER | 29-08-2021 16:45 | 29-08-2021 17:26 | 41 |  |  |  | 29-08-2021 18:20 | 1.63
Northern | K1 | TRIPPING-2021-PLS-82 | 2610/20210901/002 | Perlis | Perlis | 11kV | Underground | 01-09-2021 07:00 | PMU KANGAR CB5 | PVCB REPOH CERIA-VVIP KAN02632 CB1 | PAT KG. TANJUNG | Terminal Shorted by Animal / Insects | Partly Environment | Jumper to Drop Out Fuse Wire | OTHER | 01-09-2021 07:02 | 01-09-2021 07:18 | 16 |  |  |  | 01-09-2021 07:28 | 0.47
Northern | K1 | TRIPPING-2021-KED-481 | 0242/20210902/002 | Kedah | Jitra | 11kV | Underground | 02-09-2021 06:25 | PPU DARULAMAN 4K5 | RUMAH KEDAI 50 UNIT KJT19301 CB1 |  | Dielectric breakdown | Dielectric Deterioration | Cable Termination | OTHER | 02-09-2021 06:30 | 02-09-2021 07:10 | 40 |  |  |  | 02-09-2021 08:17 | 1.87
Northern | K1 | TRIPPING-2021-KED-487 | 0242/20210905/035 | Kedah | Jitra | 11kV | Underground | 05-09-2021 19:53 | PPU JERLUN SJ2 | KLG PROSES UDANG KERPAN KJT01685 | KLG PEOSES UDANG - KD GANDAI | Core Opened | Defective Manufacture | Cable | CABLE | 05-09-2021 19:55 | 05-09-2021 20:34 | 39 |  |  |  | 07-09-2021 05:38 | 33.75
Northern | K1 | TRIPPING-2021-PLS-83 | 2610/20210912/075 | Perlis | Perlis | 11kV | Underground | 12-09-2021 22:14 | PMU KUALA PERLIS CB3 | PMU KUALA PERLIS CB3 | PBT SG. BEREMBANG - PDB WATER TREATMENT | Insulation Failed, Shorted by Old External Damage | Partly Environment | Cable | CABLE | 12-09-2021 22:20 | 12-09-2021 22:48 | 28 | 13-09-2021 22:03 | 06-10-2021 22:00 | 551 | 07-10-2021 21:51 | 599.62
Northern | K1 | TRIPPING-2021-KED-506 | 0242/20210916/002 | Kedah | Jitra | 11kV | Underground | 16-09-2021 07:12 | PPU CHANGLOON CL5 | PPU CHANGLOON CL5 | TMN KERUING - PDT TMN TEMIN JAYA 3 | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 16-09-2021 07:26 | 16-09-2021 07:52 | 26 | 16-09-2021 15:55 | 17-09-2021 19:06 | 27 | 17-09-2021 19:21 | 36.15
Northern | K1 | TRIPPING-2021-KED-515 | 0242/20210919/006 | Kedah | Jitra | 11kV | Substation | 19-09-2021 00:46 | PPU LOJI AIR ARAU GIS 11K5 | PDB KLG BERAS PERING KJT01776 | BATU 5 - BATU 4 | Dielectric | Dielectric Deterioration | RMU SF6 | OVERHEAD LINES | 19-09-2021 00:50 | 19-09-2021 01:10 | 20 | 19-09-2021 21:46 | 20-09-2021 09:25 | 11 | 20-09-2021 09:38 | 32.87
Northern | K1 | TRIPPING-2021-KED-520 | 0242/20210920/003 | Kedah | Jitra | 11kV | Underground | 20-09-2021 05:52 | PPU JERLUN SJ2 | PPU JERLUN SJ2 |  | Dielectric breakdown | Dielectric Deterioration | Cable Termination | TRANSIENT | 20-09-2021 06:01 | 20-09-2021 06:28 | 27 |  |  |  | 20-09-2021 08:00 | 2.13
Northern | K1 | TRIPPING-2021-KED-523 | 0242/20210920/050 | Kedah | Jitra | 11kV | Substation | 20-09-2021 11:12 | PPU KODIANG KD6 | STESEN KERETAPI KODIANG KJT18950 CB1 | STESEN KERETAPI KODIANG - PAT TALIAIR 3 SANGLANG | Cable Compartment - Vermin Encroachment | Partly Environment | Circuit Breaker | CABLE | 20-09-2021 11:14 | 20-09-2021 11:53 | 39 | 20-09-2021 21:57 | 21-09-2021 03:07 | 5 | 21-09-2021 03:25 | 16.22
Northern | K1 | TRIPPING-2021-PLS-84 | 2610/20210920/067 | Perlis | Perlis | 11kV | Underground | 20-09-2021 20:53 | PMU KUALA PERLIS CB5 | PMU KUALA PERLIS CB5 | KLG AIS IGLOO - PLB LOT 764 TMN KUALA PERLIS | Core Opened | Defective Manufacture | Cable | CABLE | 20-09-2021 20:59 | 20-09-2021 21:10 | 11 | 21-09-2021 21:38 | 07-10-2021 08:22 | 370 | 07-10-2021 08:36 | 395.72
Northern | K1 | TRIPPING-2021-PLS-85 | 2610/20210920/175 | Perlis | Perlis | 11kV | Underground | 20-09-2021 22:47 | PMU KANGAR CB2 | PDB TELEKOM LAMA KANGAR KAN00551 CB1 | PLB TMN SERIAB (NOP) - PADAT TMN PERTIWI INDAH NO.2 | Core Opened | Partly Environment | Cable | CABLE | 20-09-2021 22:49 | 20-09-2021 23:21 | 32 | 21-09-2021 23:17 | 15-10-2021 09:27 | 562 | 16-10-2021 15:52 | 617.08
Northern | K1 | TRIPPING-2021-PLS-86 | RE/2610/20210811/PLS/003 | Perlis | Perlis | 11kV | Underground | 21-09-2021 04:57 | PMU CHUPING CB7 | SK GUAR NANGKA KAN02604 CB1 | RE(RSO) HBH GLOBAL ENERGY B |  |  |  | OTHER |  |  | 0 | 21-09-2021 13:01, 21-09-2021 19:08 | 21-09-2021 18:17, 22-09-2021 21:20 | 5, 26 | 22-09-2021 21:20 | 40.38
Northern | K1 | TRIPPING-2021-PLS-87 | RE/2610/20210923/PLS87 | Perlis | Perlis | 11kV | Underground | 23-09-2021 00:17 | PMU CHUPING CB7 | SK GUAR NANGKA KAN02604 CB1 | - HBH GLOBAL - |  |  |  | OTHER | 23-09-2021 00:18 | 23-09-2021 00:18 | 0 | 24-09-2021 00:29 | 24-09-2021 00:30 | 0 | 24-09-2021 00:38 | 24.35
Northern | K1 | TRIPPING-2021-PLS-88 | 2610/20210926/001 | Perlis | Perlis | 11kV | Underground | 26-09-2021 02:23 | PMU KUALA PERLIS CB10 | PMU KUALA PERLIS CB10 | PMU KUALA PERLIS CB10 - PDB TMN SEMARAK-KAN | Insulation Failed, Shorted by Old External Damage | Partly Environment | Cable | CABLE | 26-09-2021 02:26 | 26-09-2021 02:51 | 25 | 27-09-2021 21:45 | 10-10-2021 01:31 | 291 | 10-10-2021 02:10 | 335.78
Northern | K1 | TRIPPING-2021-KED-548 | 0245/20210929/018 | Kedah | Kuala Nerang | 11kV | Overhead | 29-09-2021 20:26 | PPU KUALA NERANG 6K5 | VCB SMK KUALA NERANG KNN00054 | S/S BUKIT NAMBUA - PONG MANIS | Failed and Shorted | Partly Environment | Straight Through Joint | CABLE | 29-09-2021 20:27 | 29-09-2021 20:43 | 16 | 30-09-2021 10:57 | 02-10-2021 11:08 | 48 | 02-10-2021 12:17 | 63.85
Northern | K1 | TRIPPING-2021-PLS-90 | 2610/20211003/002 | Perlis | Perlis | 11kV | Underground | 03-10-2021 03:05 | PMU KANGAR CB1 | PDB SEKOLAH VOKASIONAL KANGAR KAN00472 CB1 | PDB SK SRI INDRA - PDB PERPUSTAKAAN NEGERI-PPNPS | Insulation Failed, Shorted by Water Ingress | Under Investigation | Cable | CABLE | 03-10-2021 03:16 | 03-10-2021 03:43 | 27 | 07-10-2021 21:01 | 27-10-2021 13:09 | 472 | 28-10-2021 15:36 | 612.52
Northern | K1 | TRIPPING-2021-PLS-91 | 2610/20211004/001 | Perlis | Perlis | 11kV | Underground | 04-10-2021 00:01 | PMU KUALA PERLIS CB7 | PDB PANGSAPURI KG.WAI KAN00647 CB1 | PLB KUKUM KG. WAI - PDB PANGSAPURI KG.WAI | Core Opened | Defective Manufacture | Cable | CABLE | 04-10-2021 00:04 | 04-10-2021 00:28 | 24 | 04-10-2021 21:46 | 18-10-2021 17:31 | 331 | 18-10-2021 18:57 | 354.93
Northern | K1 | TRIPPING-2021-KED-559 | 0242/20211005/044 | Kedah | Jitra | 11kV | Underground | 05-10-2021 22:24 | PPU JERLUN SJ1 | PPU JERLUN SJ1 | TMN AROWANA - PP TALIKOM AIR HITAM | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 05-10-2021 22:31 | 05-10-2021 23:00 | 29 | 06-10-2021 12:27 | 06-10-2021 23:33 | 11 | 06-10-2021 23:50 | 25.43
Northern | K1 | TRIPPING-2021-PLS-92 | 2610/20211007/041 | Perlis | Perlis | 11kV | Underground | 07-10-2021 22:59 | PMU KANGAR CB16 | PMU KANGAR CB16 | PMU KANGAR CB16 - PDB TMN SERI PULAI 3 | Insulation Failed, Shorted by Corrosive Evmnt | Under Investigation | Cable | CABLE | 07-10-2021 23:03 | 07-10-2021 23:20 | 17 | 08-10-2021 00:41 | 21-10-2021 17:34 | 328 | 21-10-2021 18:56 | 331.95
Northern | K1 | TRIPPING-2021-PLS-93 | 2610/20211011/015 | Perlis | Perlis | 11kV | Underground | 11-10-2021 11:06 | PPU SHORUBBER CB4 | PPU SHORUBBER CB4 | PPU SHORUBBER CB4 - PDB KLJ JURURAWAT | Open Circuit | Soil Movement | Transition Joint | CABLE | 11-10-2021 11:11 | 11-10-2021 11:40 | 29 | 16-10-2021 11:48, 18-10-2021 22:41 | 17-10-2021 11:55, 19-10-2021 15:21 | 24, 16 | 19-10-2021 16:27 | 197.35
Northern | K1 | TRIPPING-2021-PLS-94 | 2610/20211013/038 | Perlis | Perlis | 11kV | Underground | 13-10-2021 22:51 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 - PDB TMN SEMATANG JAYA | Insulation Breakdown | Insulation Deterioration | Transition Joint | CABLE | 13-10-2021 22:56 | 13-10-2021 23:29 | 33 | 15-10-2021 21:58, 23-10-2021 10:31, 24-10-2021 00:14 | 22-10-2021 15:39, 23-10-2021 22:51, 25-10-2021 05:48 | 161, 12, 29 | 26-10-2021 09:56 | 299.08
Northern | K1 | TRIPPING-2021-PLS-95 | 2610/20211016/008 | Perlis | Perlis | 11kV | Overhead | 16-10-2021 07:38 | PPU PADANG BESAR CB2 | VCB PDB PEKAN KAKI BUKIT KAN00140 |  | Insulation Breakdown | Tree | Conductor | TRANSIENT | 16-10-2021 07:38 | 16-10-2021 08:30 | 52 |  |  |  | 16-10-2021 09:32 | 1.9
Northern | K1 | TRIPPING-2021-PLS-96 | 2610/20211019/019 | Perlis | Perlis | 11kV | Overhead | 19-10-2021 17:41 | PMU CHUPING CB7 | PDB KUBANG PERUN KAN00255 CB1 | SK PANGGAS - PAT KG. PADANG JELUTONG | Snapped by Trees / Branches | Partly Environment | ABC Conductor | OVERHEAD LINES | 19-10-2021 17:55 | 19-10-2021 18:32 | 37 | 20-10-2021 23:50 | 21-10-2021 21:43 | 21 | 21-10-2021 21:55 | 52.23
Northern | K1 | TRIPPING-2021-PLS-97 | 2610/20211020/031 | Perlis | Perlis | 11kV | Underground | 20-10-2021 17:43 | PPU SHORUBBER CB4 | PPU SHORUBBER CB4 | PPU SHORUBBER CB4 - PDB KLJ JURURAWAT | Open Circuit | Soil Movement | Transition Joint | CABLE | 20-10-2021 17:49 | 20-10-2021 18:07 | 18 | 21-10-2021 16:55, 22-10-2021 15:41 | 22-10-2021 10:31, 12-01-2022 03:04 | 17, 1955 | 13-01-2022 19:13 | 2041.5
Northern | K1 | TRIPPING-2021-PLS-99 | 2610/20211024/009 | Perlis | Perlis | 11kV | Underground | 24-10-2021 09:51 | PMU CHUPING CB1 | RMU CB KAJI CUACA KAN00789 | JABATAN KEBAJIKAN MASYARAKAT - SG MATI, - MASJID NGULANG - SG MATI | Core Opened | Defective Manufacture | Cable | CABLE | 24-10-2021 10:02 | 24-10-2021 10:20 | 18 | 26-10-2021 23:54 | 01-12-2021 04:01 | 844 | 01-12-2021 04:18 | 906.45
Northern | K1 | TRIPPING-2021-PLS-100 | 2610/20211026/003 | Perlis | Perlis | 11kV | Underground | 26-10-2021 04:52 | PPU SHORUBBER CB5 | BEHOR MENTALOON KAN00974 CB1 |  | Opened and Dropped | Partly Environment | Jumper to Drop Out Fuse Wire | OTHER | 26-10-2021 05:02 | 26-10-2021 05:20 | 18 |  |  |  | 26-10-2021 06:53 | 2.02
Northern | K1 | TRIPPING-PLS-21-00001 | 2610/20211101/001 | Perlis | Perlis | 11kV | Underground | 01-11-2021 00:27 | PPU PADANG BESAR CB7 | PDB KOMP KASTAM & IMIGRESEN KAN00023 CB1 | PDB BOMBA PADANG BESAR - PDB ARKED NIAGA | Insulation Failed, Shorted by Old External Damage | Under Investigation | Cable | CABLE | 01-11-2021 00:41 | 01-11-2021 01:20 | 39 | 01-11-2021 21:07 | 10-11-2021 10:29 | 205 | 10-11-2021 10:35 | 226.13
Northern | K1 | TRIPPING-KED-21-00017 | 0242/20211101/012 | Kedah | Jitra | 11kV | Underground | 01-11-2021 17:26 | PPU JERLUN SJ2 | SS 11KV SAMAK KJT19323 CB1 | PBT KUALA JERLUN 1 - PATOD JERUJU 2 | Insulation Failed, Shorted by Corrosive Evmnt | Partly Environment | Cable | CABLE | 01-11-2021 18:46 | 01-11-2021 19:18 | 32 | 02-11-2021 12:30 | 02-11-2021 18:46 | 6 | 02-11-2021 19:50 | 26.4
Northern | K1 | TRIPPING-KED-21-00020 | 0245/20211102/017 | Kedah | Kuala Nerang | 11kV | Overhead | 02-11-2021 19:41 | PPU KUALA NERANG 6K5 | PDB SMK KUALA NERANG KKN00054 | PLB BATU 19 KNG - PDT POKOK MACANG | Opened by Vandals | Act of Vandalism | ABC Conductor | CABLE | 02-11-2021 19:42 | 02-11-2021 19:50 | 8 | 03-11-2021 17:22 | 04-11-2021 22:40 | 29 | 05-11-2021 23:45 | 76.07
Northern | K1 | TRIPPING-PLS-21-00002 | 2610/20211103/003 | Perlis | Perlis | 11kV | Underground | 03-11-2021 01:32 | PPU UNIMAP GIS 2K5 | FELDA CHUPING NO.2 KAN02702 | PERLISPLANTATION - PDB RUMAH PAM JKR | Insulation Breakdown | Vandalism / Encroachment | Straight Through Joint | CABLE | 03-11-2021 02:00 | 03-11-2021 02:20 | 20 | 03-11-2021 18:07 | 03-11-2021 20:11 | 2 | 05-11-2021 01:17 | 47.75
Northern | K1 | TRIPPING-KED-21-00021 | 0245/20211103/002 | Kedah | Kuala Nerang | 11kV | Overhead | 03-11-2021 07:02 | PPU NAKA 1K5 | PPU NAKA 1K5 | PDB KEDA PONG SELATAN - PBT KG. NAHAN | Opened by Vandals | Act of Vandalism | ABC Conductor | CABLE | 03-11-2021 07:10 | 03-11-2021 07:55 | 45 | 03-11-2021 17:25 | 04-11-2021 01:31 | 8 | 04-11-2021 02:17 | 19.25
Northern | K1 | TRIPPING-KED-21-00037 | 0245/20211112/001 | Kedah | Kuala Nerang | 11kV | Underground | 12-11-2021 06:51 | PPU NAKA 1K5 | PPU NAKA 1K5 | PLB REBAN AYAM PONG - PDB INDUSTRI KEDA NAKA | Insulation Breakdown | Insulation Deterioration | Cable Termination | SWITCHGEAR | 12-11-2021 06:55 | 12-11-2021 07:23 | 28 | 13-11-2021 14:52 | 14-11-2021 09:41 | 18 | 14-11-2021 10:40 | 51.82
Northern | K1 | TRIPPING-KED-21-00038 | 0242/20211112/017 | Kedah | Jitra | 11kV | Underground | 12-11-2021 11:59 | PPU DARULAMAN 4K5 | RUMAH KEDAI 50 UNIT KJT19301 CB1 | PDB KG. KETUL-KETUL (NOP) - PATOD PADANG LIMAU | Damaged, Shorted by Third Party Dug Up | Under Investigation | Cable | CABLE | 12-11-2021 12:01 | 12-11-2021 12:30 | 29 | 13-11-2021 10:32 | 13-11-2021 23:43 | 13 | 13-11-2021 23:45 | 35.77
Northern | K1 | TRIPPING-PLS-21-00004 | 2610/20211114/005 | Perlis | Perlis | 11kV | Underground | 14-11-2021 02:55 | PPU MINI PPU ABI 11 | PPU MINI PPU ABI CB11 | CSU SPG ALOR SENA - PVCB RPA SANTAN 2 | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 14-11-2021 03:10 | 14-11-2021 03:49 | 39 | 14-11-2021 22:02 | 20-11-2021 22:53 | 144 | 20-11-2021 23:13 | 164.3
Northern | K1 | TRIPPING-PLS-21-00005 | 2610/20211114/111 | Perlis | Perlis | 11kV | Underground | 14-11-2021 05:01 | PPU BUKIT KETERI 5K5 | PDB RPA CHUPING 2 KAN00285 |  | Core Opened | Defective Manufacture | Cable | TRANSIENT | 14-11-2021 05:03 | 14-11-2021 05:08 | 5 |  |  |  | 14-11-2021 05:53 | 0.87
Northern | K1 | TRIPPING-KED-21-00042 | 0240/20211115/006 | Kedah | Kuala Nerang | 11kV | Overhead | 15-11-2021 08:48 | PPU NAKA 4K5 | PPU NAKA 4K5 |  | Insulation Breakdown | Tree | Conductor | TRANSIENT | 15-11-2021 08:49 | 15-11-2021 09:05 | 16 |  |  |  | 15-11-2021 09:50 | 1.03
Northern | K1 | TRIPPING-PLS-21-00006 | 2610/20211115/016 | Perlis | Perlis | 11kV | Underground | 15-11-2021 15:31 | PMU CHUPING CB1 | PMU CHUPING CB1 | PBT KG. BALIK BUKIT - PAT BAWAH BUKIT | Damaged, Shorted by Third Party Dug Up | Under Investigation | Cable | CABLE | 15-11-2021 15:33 | 15-11-2021 16:00 | 27 | 15-11-2021 16:21, 15-11-2021 21:57, 19-11-2021 10:53 | 15-11-2021 16:46, 19-11-2021 10:52, 19-11-2021 19:07 | 0, 84, 8 | 19-11-2021 20:00 | 100.48
Northern | K1 | TRIPPING-KED-21-00044 | 0242/20211115/018 | Kedah | Jitra | 11kV | Underground | 15-11-2021 17:37 | PPU KODIANG KD2 | PDB SM TUNKU BENDAHARA KJT01260 CB1 | PBT KG. WANG - PDB KLG BERAS KBG MENERONG | Insulation Failed, Shorted by Old External Damage | Partly Environment | Cable | CABLE | 15-11-2021 17:40 | 15-11-2021 18:18 | 38 | 16-11-2021 15:23 | 16-11-2021 22:26 | 7 | 16-11-2021 22:35 | 28.97
Northern | K1 | TRIPPING-KED-21-00047 | 0245/20211119/017 | Kedah | Kuala Nerang | 11kV | Overhead | 19-11-2021 18:55 | PPU KUALA NERANG 9K5 | PDB TMN AKASIA KKN00582 | PDB TMN AKASIA - PADAT LDG BUKIT NGAUN | Insulation Breakdown | Insulation Deterioration | Conductor | CABLE | 19-11-2021 18:58 | 19-11-2021 19:11 | 13 | 20-11-2021 01:08 | 21-11-2021 02:38 | 25 | 21-11-2021 02:30 | 31.58
Northern | K1 | TRIPPING-PLS-21-00007 | RE/2610/20211121/PLS/0007 | Perlis | Perlis | 11kV | Underground | 21-11-2021 06:18 | PMU CHUPING CB7 | SK GUAR NANGKA KAN02604 CB1 | SK GUAR NANGKA KAN02604 - RE(RSO) HBH GLOBAL ENERGY B |  |  |  | CABLE | 21-11-2021 06:24 |  | 0 | 21-11-2021 13:27 | 25-11-2021 23:36 | 106 | 25-11-2021 23:49 | 113.52
Northern | K1 | TRIPPING-KED-21-00049 | 0242/20211121/074 | Kedah | Jitra | 11kV | Underground | 21-11-2021 20:43 | PPU JERLUN SJ2 | PPU JERLUN SJ2 | PPU JERLUN SJ2 - PDB KLG PROSES UDANG KERPAN KJT01686 | Core Opened | Partly Environment | Cable | CABLE | 21-11-2021 20:47 | 21-11-2021 21:10 | 23 | 21-11-2021 23:24, 25-11-2021 17:32, 25-11-2021 16:24 | 25-11-2021 16:23, 25-11-2021 22:17, 25-11-2021 22:26 | 88, 4, 6 | 25-11-2021 22:26 | 97.72
Northern | K1 | TRIPPING-KED-21-00054 | 0242/20211123/017 | Kedah | Jitra | 11kV | Underground | 23-11-2021 16:15 | PPU DARULAMAN 4K5 | RUMAH KEDAI 50 UNIT KJT19301 CB1 | PAT KG GELONG RAMBAI KJT01743 - PAT KG. PDG LIMAU KJT18367 | Insulation Breakdown | Insulation Deterioration | Conductor | CABLE | 23-11-2021 16:22 | 23-11-2021 16:40 | 18 | 24-11-2021 21:53, 25-11-2021 03:01 | 25-11-2021 02:56, 25-11-2021 03:14 | 5, 0 | 25-11-2021 03:23 | 35.13
Northern | K1 | TRIPPING-KED-21-00058 | 0242/20211127/003 | Kedah | Jitra | 11kV | Underground | 27-11-2021 08:20 | PMU TANJUNG PAUH TP19 | PMU TANJUNG PAUH TP19 | PMU TANJUNG PAUH TP19 - PDB JITRA MALL KJT00544 | Failed, Shorted by Old External Damage | Partly Environment | Straight Through Joint | CABLE | 27-11-2021 08:23 | 27-11-2021 09:05 | 42 | 29-11-2021 23:47 | 30-11-2021 07:56 | 8 | 30-11-2021 08:30 | 72.17
Northern | K1 | TRIPPING-KED-21-00062 | 0242/20211128/048 | Kedah | Jitra | 11kV | Underground | 28-11-2021 23:43 | PPU JERLUN SJ2 | 11KV SAMAK KJT01663 | PDB KLG BERAS MAKLUM JAYA KJT01722 | Dielectric breakdown | Dielectric Deterioration | Cable Termination | TRANSIENT | 29-11-2021 00:34 | 29-11-2021 00:37 | 3 |  |  |  | 29-11-2021 02:07 | 2.4
Northern | K1 | TRIPPING-KED-21-00068 | 0245/20211204/001 | Kedah | Kuala Nerang | 11kV | Underground | 04-12-2021 04:35 | PPU KUALA NERANG 7K5 | A/R KG. TENGAH | PAT KG. BAYAS-ALS KKN00741 - PBT SM AGAMA TOK LATAH KJT19001 | Insulation Breakdown | Insulation Deterioration | Cable Termination | CABLE | 04-12-2021 07:41 | 04-12-2021 07:55 | 14 | 04-12-2021 18:01 | 05-12-2021 02:29 | 8 | 05-12-2021 02:45 | 22.17
Northern | K1 | TRIPPING-PLS-21-00009 | 2610/20211206/035 | Perlis | Perlis | 11kV | Underground | 06-12-2021 14:44 | PMU KANGAR CB1 | PDB SEKOLAH VOKASIONAL KANGAR KAN00472 CB1 | PDB SK SRI INDRA KAN00470 - PDB PERPUSTAKAAN NEGERI-PPNPS KAN00469 | Open Circuit | Improper Installation | Straight Through Joint | CABLE | 06-12-2021 14:50 | 06-12-2021 15:05 | 15 | 06-12-2021 16:37 | 11-12-2021 05:46 | 109 | 11-12-2021 06:09 | 111.42
Northern | K1 | TRIPPING-KED-21-00073 | 0242/20211207/004 | Kedah | Jitra | 11kV | Underground | 07-12-2021 09:40 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01798 CB1 |  | Dielectric breakdown | Dielectric Deterioration | Cable Termination | NO FAULT | 07-12-2021 09:41 | 07-12-2021 10:07 | 26 |  |  |  | 07-12-2021 11:13 | 1.55
Northern | K1 | TRIPPING-PLS-21-00010 | 2610/20211208/043 | Perlis | Perlis | 11kV | Overhead | 08-12-2021 16:19 | PPU BUKIT KETERI 7K5 | PPU BUKIT KETERI 7K5 | PPU BUKIT KETERI 7K5 - PDB TMN BESERI JAYA KAN00177 | Insulation Breakdown | Animal | Conductor | CABLE | 08-12-2021 16:19 | 08-12-2021 16:49 | 30 | 08-12-2021 22:35 | 09-12-2021 21:09 | 22 | 09-12-2021 21:40 | 29.35
Northern | K1 | TRIPPING-PLS-21-00011 | 2610/20211212/023 | Perlis | Perlis | 11kV | Underground | 12-12-2021 22:02 | PMU KUALA PERLIS CB10 | PDB IKBN KAN00655 | PDB IKBN KAN00655 - PDB WANG PINANG KAN00654 |  |  |  | CABLE |  | 12-12-2021 23:20 | 0 | 13-12-2021 11:19 | 13-12-2021 17:15 | 5 | 13-12-2021 17:27 | 19.42
Northern | K1 | TRIPPING-KED-21-00089 | 0242/20211215/035 | Kedah | Jitra | 11kV | Underground | 15-12-2021 18:15 | PPU CHANGLOON CL4 | PPU CHANGLOON CL4 | PDB TMN ANGSANA-JITRA - PDB TMN JELUTONG | Dielectric breakdown | Dielectric Deterioration | Straight Through Joint | CABLE | 15-12-2021 18:25 | 15-12-2021 18:45 | 20 | 16-12-2021 00:38 | 24-12-2021 03:18 | 194 | 24-12-2021 03:48 | 201.55
Northern | K1 | TRIPPING-PLS-21-00012 | 2610/20211216/017 | Perlis | Perlis | 11kV | Underground | 16-12-2021 16:42 | PPU PADANG BESAR CB2 | PDB PEKAN KAKI BUKIT KAN00137 | PDB GUA KELAM PEKAN KAKI BUKIT KAN00134 | Dielectric breakdown | Dielectric Deterioration | Cable Termination | TRANSIENT | 16-12-2021 17:00 | 16-12-2021 17:34 | 34 |  |  |  | 16-12-2021 19:09 | 2.45
Northern | K1 | TRIPPING-KED-21-00093 | 0242/20211217/001 | Kedah | Jitra | 11kV | Underground | 17-12-2021 01:40 | PPU CHANGLOON CL6 | PPU CHANGLOON CL6 | STN SUIS R/AWAM CHANGLUN KJT00793 - TMN CASUARINA KJT01810 | Core Opened | Defective Manufacture | Cable | CABLE | 17-12-2021 01:44 | 17-12-2021 02:41 | 57 | 17-12-2021 14:40 | 19-12-2021 06:54 | 40 | 20-12-2021 10:14 | 80.57
Northern | K1 | TRIPPING-KED-21-00103 | 0242/20211223/018 | Kedah | Jitra | 11kV | Underground | 23-12-2021 19:18 | PPU PELUBANG PL3 | PDB SK PENGHULU HJ DARUS KJT00700 CB1 | PBT KG. LEMBAH ARANG KJT18894 - SSL KUALA PAI KJT18893 | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 23-12-2021 19:20 | 23-12-2021 20:02 | 42 | 24-12-2021 19:19 | 25-12-2021 18:25 | 23 | 25-12-2021 19:25 | 48.12
Northern | K1 | TRIPPING-PLS-21-00013 | 2610/20211227/010 | Perlis | Perlis | 11kV | Underground | 27-12-2021 12:46 | PMU KANGAR CB7 | TMN BUNGA PADI KAN00388 CB1 | PDB LPP BINTONG KAN00400 - TMN BUNGA PADI KAN00388 |  |  |  | CABLE |  | 27-12-2021 13:20 | 0 | 27-12-2021 16:05 | 04-01-2022 16:09 | 192 | 05-01-2022 17:41 | 220.92
Northern | K1 | TRIPPING-PLS-21-00014 | 2610/20211227/041 | Perlis | Perlis | 11kV | Underground | 27-12-2021 18:00 | PPU PADANG BESAR CB2 | PDB GUA KELAM PEKAN KAKI BUKIT KAN02865 | PLKN KAKI BUKIT KAN02866 | Dielectric breakdown | Dielectric Deterioration | Cable Termination | TRANSIENT | 27-12-2021 21:23 | 27-12-2021 21:27 | 4 |  |  |  | 27-12-2021 22:03 | 4.05
Northern | K1 | TRIPPING-PLS-21-00015 | 2610/20211230/028 | Perlis | Perlis | 11kV | Underground | 30-12-2021 17:39 | PPU PADANG BESAR CB12 | PVCB QTRS KTMB KAN02219 CB1 | PVCB QTRS KTMB KAN02219 - PLB KG. KOLAM 1 KAN00043, - PLB KG. KOLAM 1 KAN00041 - RPA PADANG BESAR KAN00039, - PLB KG. KOLAM 1 KAN00042 - UKK PADANG BESAR KAN00044 | Damaged, Shorted by Third Party Dug Up | Under Investigation | Cable | CABLE, CABLE, CABLE | 30-12-2021 17:52 | 30-12-2021 18:22 | 30 | 30-12-2021 23:52, 31-12-2021 01:12, 31-12-2021 02:55, 23-03-2022 12:11, 12-04-2022 14:10 | 31-12-2021 00:41, 04-01-2022 22:27, 04-01-2022 22:27, 24-03-2022 18:30, 13-04-2022 20:47 | 0, 117, 115, 30, 30 | 13-04-2022 21:18 | 2499.65
Northern | K1 | TRIPPING-PLS-22-00001 | 2610/20220101/039 | Perlis | Perlis | 11kV | Underground | 01-01-2022 11:36 | PMU KANGAR CB4 | PDB TMN SHAHRIZAD KAN00686 CB1 | CSU TMN PUTRA UTAMA NO.3 KAN03157 - SSU GIANT KGAR KAN02771 |  |  |  | CABLE | 01-01-2022 11:41 | 01-01-2022 11:59 | 18 | 02-01-2022 11:45 | 02-01-2022 17:42 | 5 | 02-01-2022 18:15 | 30.65
Northern | K1 | TRIPPING-KED-22-00002 | 0242/20220101/018 | Kedah | Jitra | 11kV | Overhead | 01-01-2022 17:08 | PPU CHANGLOON CL5 | PPU CHANGLOON CL5 |  | Insulation Failed and Shorted | Partly Environment | Cable Termination | TRANSIENT | 01-01-2022 17:10 | 01-01-2022 17:55 | 45 |  |  |  | 01-01-2022 18:43 | 1.58
Northern | K1 | TRIPPING-KED-22-00004 | 0242/20220104/001 | Kedah | Jitra | 11kV | Underground | 04-01-2022 07:32 | PPU CHANGLOON CL6 | PPU CHANGLOON CL6 | TMN CASUARINA - S/S RUMAH AWAM CHANGLUN | Open Circuit | Soil Movement | Straight Through Joint | CABLE | 04-01-2022 07:48 | 04-01-2022 08:25 | 37 | 04-01-2022 22:24 | 08-01-2022 23:20 | 96 | 08-01-2022 23:46 | 112.23
Northern | K1 | TRIPPING-PLS-22-00002 | 2610/20220110/014 | Perlis | Perlis | 11kV | Underground | 10-01-2022 13:23 | PMU KUALA PERLIS CB2 | TMN BUNGA PADI KAN00386 CB1 | PDB RUMAH ANAK YATIM MAK TEH KAN02006 - BESI HANGIT(KG PONDOK)-VVIP KAN00375 | Dielectric breakdown | Contamination | Cable Termination | CABLE | 10-01-2022 13:25 | 10-01-2022 13:45 | 20 | 11-01-2022 21:23 | 12-01-2022 01:47 | 4 | 12-01-2022 02:10 | 36.78
Northern | K1 | TRIPPING-PLS-22-00003 | 2610/20220110/075 | Perlis | Perlis | 11kV | Underground | 10-01-2022 23:12 | PMU KUALA PERLIS CB10 | PDB TMN SEMARAK KAN00660 | PLB KLG HAI SOON KAN00668 - PDB BALAI BOMBA KUALA PERLIS KAN01905, - PMUKUALA PERLIS CB10 - PDB TMN SEMARAK-KAN KAN00659 |  |  |  | CABLE, CABLE |  | 10-01-2022 23:57 | 0 | 11-01-2022 01:13, 11-01-2022 14:39, 11-01-2022 23:28, 16-01-2022 11:25, 23-01-2022 21:47 | 11-01-2022 01:25, 22-01-2022 21:08, 12-01-2022 01:34, 18-01-2022 12:43, 24-01-2022 19:06 | 0, 270, 2, 49, 21 | 24-01-2022 19:10 | 331.97
Northern | K1 | TRIPPING-PLS-22-00004 | 2610/20220118/001 | Perlis | Perlis | 11kV | Underground | 18-01-2022 07:34 | PPU SIMPANG EMPAT CB9 | PPU SIMPANG EMPAT CB9 | PAT PADANG BENTA KAN01223 | Dielectric breakdown | Contamination | Cable Termination | TRANSIENT | 18-01-2022 07:35 | 18-01-2022 08:10 | 35 |  |  |  | 18-01-2022 08:23 | 0.82
Northern | K1 | TRIPPING-PLS-22-00005 | 2610/20220123/017 | Perlis | Perlis | 11kV | Underground | 23-01-2022 22:26 | PPU SHORUBBER CB6 | PPU SHORUBBER CB6 | PPU SHORUBBER CB6 - PDB POLIKLINIK ARAU KAN00901 | Damaged, Soil Movement | Under Investigation | Cable | CABLE | 23-01-2022 22:29 | 23-01-2022 22:52 | 23 | 24-01-2022 22:46 | 09-02-2022 07:53 | 369 | 10-02-2022 20:54 | 430.47
Northern | K1 | TRIPPING-KED-22-00037 | 0242/20220125/002 | Kedah | Jitra | 11kV | Underground | 25-01-2022 04:44 | PPU DARULAMAN 9K5 | PPU DARULAMAN 9K5 |  | Dielectric breakdown | Contamination | Cable Termination | NO FAULT | 25-01-2022 05:00 | 25-01-2022 05:40 | 40 |  |  |  | 25-01-2022 06:42 | 1.97
Northern | K1 | TRIPPING-KED-22-00040 | 0242/20220126/003 | Kedah | Jitra | 11kV | Underground | 26-01-2022 09:59 | PPU PELUBANG PL3 | PDB SK PENGHULU HJ DARUS KJT00694 CB1 |  |  |  |  | TRANSIENT |  | 26-01-2022 10:40 | 0 |  |  |  | 26-01-2022 13:28 | 3.48
Northern | K1 | TRIPPING-PLS-22-00006 | 2610/20220129/005 | Perlis | Perlis | 11kV | Underground | 29-01-2022 10:57 | PPU PADANG BESAR CB10 | UKK PADANG BESAR KAN00047 CB1 | PDB NORTHERN DOLOMITE KAN02176 - SK FELDA RIMBA MAS KAN03084 | Core Opened | Defective Manufacture | Cable | CABLE | 29-01-2022 11:20 | 29-01-2022 11:40 | 20 | 30-01-2022 10:08 | 31-01-2022 18:25 | 32 | 31-01-2022 18:39 | 55.7
Northern | K1 | TRIPPING-PLS-22-00007 | 2610/20220129/047 | Perlis | Perlis | 11kV | Underground | 29-01-2022 21:41 | PPU SIMPANG EMPAT CB6 | PPU SIMPANG EMPAT CB6 | TMN KAYANG PERMAI KAN03093 - TMN SIMPANG INDAH KAN02758 | Open Circuit | Soil Movement | Straight Through Joint | CABLE | 29-01-2022 21:44 | 29-01-2022 22:12 | 28 | 30-01-2022 12:21 | 04-02-2022 00:25 | 108 | 04-02-2022 00:42 | 123.02
Northern | K1 | TRIPPING-PLS-22-00008 | 2610/20220130/002 | Perlis | Perlis | 11kV | Underground | 30-01-2022 03:23 | PPU SIMPANG EMPAT CB3 | PPU SIMPANG EMPAT CB3 | PBT MENGKUANG LAYAR KAN01066 - PATOD UJUNG BATU KAN01067 | Core Opened | Partly Environment | Cable | CABLE | 30-01-2022 03:33 | 30-01-2022 04:00 | 27 | 30-01-2022 21:09 | 16-02-2022 19:33 | 406 | 16-02-2022 19:44 | 424.35
Northern | K1 | TRIPPING-KED-22-00052 | 0242/20220203/025 | Kedah | Jitra | 11kV | Underground | 03-02-2022 18:06 | PMU BUKIT KAYU HITAM BKH4 | PMU BUKIT KAYU HITAM BKH4 | PDB KOMP CHANGLUN 2 KJT00802 - STN SUIS R/AWAM CHANGLUN KJT00801, - S/S RMU BATU 26 KJT00818 - PATOD BATU 25 KJT00817 |  |  |  | CABLE, CABLE | 03-02-2022 18:10 | 03-02-2022 18:45 | 35 | 03-02-2022 23:43, 03-02-2022 23:45 | 06-02-2022 12:16, 06-02-2022 12:14 | 60, 60 | 06-02-2022 22:38 | 76.53
Northern | K1 | TRIPPING-KED-22-00060 | 0245/20220208001 | Kedah | Kuala Nerang | 11kV | Overhead | 08-02-2022 07:56 | PPU KUALA NERANG 5K5 | A/R TG SEBERANG | PBT PADANG CENDERAI - PBT PADANG SANAI | Core Opened | Defective Manufacture | Cable | CABLE | 08-02-2022 07:48 | 08-02-2022 07:50 | 2 | 08-02-2022 14:19 | 09-02-2022 09:53 | 19 | 09-02-2022 10:07 | 26.18
Northern | K1 | TRIPPING-PLS-22-00009 | 2610/20220218/034 | Perlis | Perlis | 11kV | Underground | 18-02-2022 23:27 | PPU SHORUBBER CB6 | PPU SHORUBBER CB6 | PPU SHORUBBER CB6 - PDB POLIKLINIK ARAU KAN00901 | Core Opened | Defective Manufacture | Cable | CABLE | 18-02-2022 23:33 | 19-02-2022 00:14 | 41 | 19-02-2022 22:12, 04-04-2022 12:11 | 04-04-2022 10:54, 05-04-2022 15:51 | 1044, 27 | 06-04-2022 16:09 | 1120.7
Northern | K1 | TRIPPING-PLS-22-00010 | 2610/20220220/004 | Perlis | Perlis | 11kV | Underground | 20-02-2022 07:22 | PMU KANGAR CB5 | PVCB REPOH CERIA-VVIP KAN02632 CB1 | PAT KG. TANJUNG KAN00765 - | Insulation Burnt | Partly Environment | Cable Termination | OVERHEAD LINES | 20-02-2022 07:36 | 20-02-2022 08:00 | 24 |  |  |  | 21-02-2022 03:55 | 20.55
Northern | K1 | TRIPPING-PLS-22-00011 | RE/2610/20220222/PLS/00011 | Perlis | Perlis | 11kV | Underground | 22-02-2022 12:02 | PPU PADANG BESAR CB16 | PPU PADANG BESAR CB16 |  |  |  |  | NO FAULT | 22-02-2022 12:05 | 22-02-2022 12:45 | 40 | 22-02-2022 13:39, 22-02-2022 13:40, 22-02-2022 21:20 | 22-02-2022 13:39, 22-02-2022 20:22, 24-02-2022 00:40 | 0, 6, 27 | 24-02-2022 00:48 | 36.77
Northern | K1 | TRIPPING-PLS-22-00012 | 2610/20220223/058 | Perlis | Perlis | 11kV | Underground | 23-02-2022 17:46 | PPU LOJI AIR ARAU GIS 3K5 | PDB POLIKLINIK ARAU KAN00898 CB1 | PDT C/S DEWAN SIVIK - PDB RUMAH PAM ARAU KAN00848 | Core Opened | Partly Environment | Cable | CABLE | 23-02-2022 17:56 | 23-02-2022 18:10 | 14 | 24-02-2022 18:13 | 04-03-2022 10:03 | 183 | 04-03-2022 10:24 | 208.63
Northern | K1 | TRIPPING-KED-22-00093 | 0242/20220226/159 | Kedah | Jitra | 11kV | Underground | 26-02-2022 10:13 | PPU KODIANG KD2 | PDB SM TUNKU BENDAHARA KJT01255 CB1 | PDB SM TUNKU BENDAHARA KJT01255 - PBT KG. BARU TOK ARANG KJT01261 | Core Opened | Partly Environment | Cable | CABLE | 26-02-2022 10:16 | 26-02-2022 10:56 | 40 | 26-02-2022 15:39 | 02-03-2022 04:45 | 85 | 02-03-2022 18:35 | 104.37
Northern | K1 | TRIPPING-PLS-22-00014 | 2610/20220226/011 | Perlis | Perlis | 11kV | Underground | 26-02-2022 11:24 | PMU KUALA PERLIS CB10 | PDB TMN SEMARAK KAN00657 CB1 | PDB IKBN KAN00656 - PDB TMN SEMARAK-KAN KAN00657 |  |  |  | CABLE | 26-02-2022 11:26 | 26-02-2022 12:05 | 39 | 26-02-2022 18:08 | 05-03-2022 18:58 | 168 | 05-03-2022 19:23 | 175.98
Northern | K1 | TRIPPING-PLS-22-00015 | 2610/20220228/013 | Perlis | Perlis | 11kV | Underground | 28-02-2022 11:23 | PMU KUALA PERLIS CB1 | PMU KUALA PERLIS CB1 | PMU KUALA PERLIS CB1 - PDB PROMENADE KAN01200 | Core Opened | Defective Manufacture | Cable | CABLE | 28-02-2022 11:23 | 28-02-2022 11:42 | 19 | 01-03-2022 00:33 | 08-03-2022 18:40 | 186 | 08-03-2022 19:35 | 200.2
Northern | K1 | TRIPPING-PLS-22-00016 | RE/2610/20220228/PLS/00016 | Perlis | Perlis | 11kV | Underground | 28-02-2022 14:15 | PPU UNIMAP GIS 15K5 | PPU UNIMAP GIS 15K5 |  |  |  |  | NO FAULT | 28-02-2022 14:17 | 28-02-2022 14:50 | 33 | 28-02-2022 15:05 | 02-03-2022 15:23 | 48 | 02-03-2022 15:40 | 49.42
Northern | K1 | TRIPPING-PLS-22-00018 | 2610/20220303/050 | Perlis | Perlis | 11kV | Underground | 03-03-2022 23:41 | PPU MINI PPU ABI 11 | PPU MINI PPU ABI CB11 | PAT SMPG SG SIRAN KAN00349 - | Insulation Breakdown | Insulation Deterioration | Cable Termination | TRANSIENT | 04-03-2022 00:27 | 04-03-2022 00:46 | 19 |  |  |  | 04-03-2022 01:03 | 1.37
Northern | K1 | TRIPPING-KED-22-00110 | 0245/20220308/002 | Kedah | Kuala Nerang | 11kV | Overhead | 08-03-2022 03:28 | PPU KUALA NERANG 6K5 | PPU KUALA NERANG 6K5 | PBT KG. SEMELIANG-VVIP KKN00635 - PDB HOSPITAL KUALA NERANG KKN00020 | Core Opened | Defective Manufacture | Cable | CABLE | 08-03-2022 03:30 | 08-03-2022 04:06 | 36 | 08-03-2022 14:19 | 12-03-2022 00:22 | 82 | 12-03-2022 00:25 | 92.95
Northern | K1 | TRIPPING-PLS-22-00020 | 2610/20220309/027 | Perlis | Perlis | 11kV | Underground | 09-03-2022 20:14 | PPU PADANG BESAR CB11 | PPU PADANG BESAR CB11 | PDB UPP PADANG BESAR KAN00049 - UKK PADANG BESAR KAN00048 | Open Circuit | Soil Movement | Straight Through Joint | CABLE | 09-03-2022 20:15 | 09-03-2022 20:50 | 35 | 10-03-2022 14:38, 10-03-2022 17:07, 23-03-2022 18:52 | 10-03-2022 14:48, 13-03-2022 14:40, 24-03-2022 18:55 | 0, 69, 24 | 24-03-2022 19:00 | 358.77
Northern | K1 | TRIPPING-KED-22-00115 | 0242/20220311/023 | Kedah | Jitra | 11kV | Underground | 11-03-2022 08:47 | PMU BUKIT KAYU HITAM BKH8 | STN SUIS ICQS KJT19258 | PLUS BKH KJT19275 - PATOD POS KAWALAN SEMPADAN KJT19167 | Core Opened | Defective Manufacture | Cable | CABLE | 11-03-2022 10:36 | 11-03-2022 11:23 | 47 | 12-03-2022 17:17 | 13-03-2022 11:55 | 18 | 13-03-2022 12:17 | 51.5
Northern | K1 | TRIPPING-KED-22-00116 | 0245/20220311/002 | Kedah | Kuala Nerang | 11kV | Underground | 11-03-2022 12:07 | PPU NAKA 6K5 | PPU NAKA 6K5 | PBT KG. LUBOK RAMBAI KKN00623 - PLB KEDA KG. BAGAN KKN00427 | Failed, Shorted by Water Ingress | Partly Environment | Transition Joint | CABLE | 11-03-2022 12:08 | 11-03-2022 12:50 | 42 | 11-03-2022 16:39 | 12-03-2022 18:59 | 26 | 12-03-2022 19:25 | 31.3
Northern | K1 | TRIPPING-PLS-22-00023 | 2610/20220314/025 | Perlis | Perlis | 11kV | Underground | 14-03-2022 18:22 | PPU PADANG BESAR CB7 | PDB KOMP KASTAM & IMIGRESEN KAN00023 CB1 | PDB KOMP KASTAM & IMIGRESEN KAN00023 - PDB STESEN BAS PADANG BESAR KAN00024 | Core Opened | Defective Manufacture | Cable | CABLE | 14-03-2022 18:23 | 14-03-2022 19:00 | 37 | 15-03-2022 01:54 | 15-03-2022 16:36 | 14 | 15-03-2022 17:15 | 22.88
Northern | K1 | TRIPPING-KED-22-00126 | 0240/20220321/001 | Kedah | Jitra | 11kV | Underground | 21-03-2022 01:43 | PPU DARULAMAN 4K5 | RUMAH KEDAI 50 UNIT KJT19301 CB1 | SSL SG. BUDI KJT00368 - PBT CHANGKAT BUDI (NOP) KJT00369 | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 21-03-2022 02:02 | 21-03-2022 02:37 | 35 | 21-03-2022 22:05 | 29-03-2022 09:32 | 179 | 29-03-2022 09:45 | 200.03
Northern | K1 | TRIPPING-PLS-22-00024 | 2610/20220321/004 | Perlis | Perlis | 11kV | Underground | 21-03-2022 02:37 | PMU KUALA PERLIS CB3 | PMU KUALA PERLIS CB3 | PDB LOJI AIR SG. BARU KAN01143 - PDT RUMAH PAM SMPG EMPAT KAN01144 | Core Opened | Defective Manufacture | Cable | CABLE | 21-03-2022 02:59 | 21-03-2022 03:10 | 11 | 21-03-2022 21:34, 07-04-2022 21:31 | 05-04-2022 22:53, 11-04-2022 18:50 | 361, 93 | 12-04-2022 21:38 | 547.02
Northern | K1 | TRIPPING-PLS-22-00025 | 2610/20220321/104 | Perlis | Perlis | 11kV | Underground | 21-03-2022 21:47 | PPU SIMPANG EMPAT CB5 | PPU SIMPANG EMPAT CB5 | CSU TANGKI AIR SIMPANG 4 KAN03194 - SEK MEN SANGLANG KAN01093 | Core Opened | Partly Environment | Cable | CABLE | 21-03-2022 21:49 | 21-03-2022 22:15 | 26 | 22-03-2022 23:39 | 07-04-2022 13:25 | 373 | 08-04-2022 12:21 | 422.57
Northern | K1 | TRIPPING-PLS-22-00026 | RE/2610/20220322/PLS/00026 | Perlis | Perlis | 11kV | Underground | 22-03-2022 10:50 | PMU CHUPING CB7 | SK GUAR NANGKA KAN02604 CB1 |  |  |  |  | NO FAULT | 22-03-2022 10:51 |  | 0 |  |  |  | 22-03-2022 22:35 | 11.75
Northern | K1 | TRIPPING-PLS-22-00027 | 2610/20220323/042 | Perlis | Perlis | 11kV | Underground | 23-03-2022 21:12 | PPU SHORUBBER CB5 | BEHOR MENTALOON KAN00975 CB1 | PDB KLG PADI MAJU KAN01039 - PPU SIMPANG EMPAT CB1 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 23-03-2022 21:14 | 23-03-2022 21:55 | 41 | 25-03-2022 11:09 | 26-03-2022 23:25 | 36 | 27-03-2022 00:37 | 75.42
Northern | K1 | TRIPPING-PLS-22-00028 | 2610/20220325/017 | Perlis | Perlis | 11kV | Underground | 25-03-2022 18:28 | PPU PADANG BESAR CB2 | PDB GUA KELAM PEKAN KAKI BUKIT KAN00134 |  | Core Opened | Defective Manufacture | Cable | TRANSIENT |  | 25-03-2022 21:21 | 0 |  |  |  | 25-03-2022 22:01 | 3.55
Northern | K1 | TRIPPING-KED-22-00143 | 0245/20220328/011 | Kedah | Kuala Nerang | 11kV | Underground | 28-03-2022 12:44 | PPU NAKA 6K5 | PPU NAKA 6K5 | PBT KG. CHANDING KKN00419 - PLT SK LAMDIN KKN00421 | Damaged, Shorted by Third Party Dug Up | Lack of Maintenance | Cable | CABLE | 28-03-2022 12:57 | 28-03-2022 13:20 | 23 | 28-03-2022 22:06 | 29-03-2022 19:35 | 21 | 29-03-2022 23:34 | 34.83
Northern | K1 | TRIPPING-PLS-22-00030 | 2610/20220329/042 | Perlis | Perlis | 11kV | Underground | 29-03-2022 22:17 | PPU SIMPANG EMPAT CB7 | PPU SIMPANG EMPAT CB7 | PPU SIMPANG EMPAT CB7 - TMN PELANGI-KAN KAN01805 | Core Opened | Partly Environment | Cable | CABLE | 29-03-2022 22:20 | 29-03-2022 22:30 | 10 | 30-03-2022 22:37, 11-04-2022 10:38 | 11-04-2022 10:32, 11-04-2022 20:26 | 275, 9 | 12-04-2022 21:28 | 335.18
Northern | K1 | TRIPPING-PLS-22-00031 | 2610/20220330/007 | Perlis | Perlis | 11kV | Underground | 30-03-2022 09:22 | PPU SHORUBBER CB8 | PDB TMN HARMONI KANGAR KAN01925 CB1 | TMN HJ MOKHTAR KAN03004 - PDB TMN HARMONI KANGAR KAN01925 | Insulation Failed, Shorted by Water Ingress | Under Investigation | Cable | CABLE | 30-03-2022 09:31 | 30-03-2022 10:08 | 37 | 04-04-2022 12:08 | 04-04-2022 16:15 | 4 | 04-04-2022 16:27 | 127.08
Northern | K1 | TRIPPING-KED-22-00154 | 0242/20220401/042 | Kedah | Jitra | 11kV | Underground | 01-04-2022 10:22 | PPU DARULAMAN 4K5 | PLB PULAU KECIL KJT00057 CB1 |  | Insulation Failed, Shorted by Corrosive Evmnt | Partly Environment | Cable | NO FAULT | 01-04-2022 10:43 | 01-04-2022 11:20 | 37 |  |  |  | 01-04-2022 12:00 | 1.63
Northern | K1 | TRIPPING-PLS-22-00032 | 2610/20220402/001 | Perlis | Perlis | 11kV | Underground | 02-04-2022 06:02 | PPU BUKIT KETERI 5K5 | PPU BUKIT KETERI 5K5 | PLB PMU BUKIT KETERI (L) - MEDAN CHUPING JAYA KAN02736 | Core Opened | Defective Manufacture | Cable | CABLE |  | 02-04-2022 06:40 | 0 | 02-04-2022 15:32 | 05-04-2022 15:18 | 71 | 05-04-2022 15:30 | 81.47
Northern | K1 | TRIPPING-PLS-22-00033 | 2610/20220403/004 | Perlis | Perlis | 11kV | Overhead | 03-04-2022 06:44 | PPU SHORUBBER CB5 | BEHOR MENTALOON KAN00974 CB1 |  | Insulation Failed and Shorted | Partly Environment | Cable Termination | TRANSIENT |  | 03-04-2022 07:24 | 0 |  |  |  | 03-04-2022 08:15 | 1.52
Northern | K1 | TRIPPING-PLS-22-00034 | 2610/20220404/004 | Perlis | Perlis | 11kV | Underground | 04-04-2022 08:58 | PPU BUKIT KETERI 3K5 | PVCB PANGGAS KAN00281 | PBT GUAR PANJI KAN00214 - PBT BILAL UDOH KAN00215 | Core Opened | Defective Manufacture | Cable | NO FAULT |  | 04-04-2022 09:30 | 0 | 04-04-2022 23:32 | 05-04-2022 15:34 | 16 | 05-04-2022 16:11 | 31.22
Northern | K1 | TRIPPING-PLS-22-00035 | RE/2610/20220406/PLS/35 | Perlis | Perlis | 11kV | Underground | 06-04-2022 04:38 | PPU UNIMAP GIS 15K5 | PPU UNIMAP GIS 15K5 | RE(ASO) MUNSANG PLANTATION B - |  |  |  | TRANSIENT | 06-04-2022 05:50 | 06-04-2022 06:55 | 65 |  |  |  | 06-04-2022 10:02 | 5.4
Northern | K1 | TRIPPING-PLS-22-00036 | RE/2610/20220406/PLS/36 | Perlis | Perlis | 11kV | Underground | 06-04-2022 04:38 | PPU UNIMAP GIS 15K5 | PPU UNIMAP GIS 15K5 | RE(RSO) SBU POWER (LSS) B - |  |  |  | SWITCHGEAR | 06-04-2022 05:50 | 06-04-2022 06:55 | 65 |  |  |  | 09-04-2022 17:45 | 85.12
Northern | K1 | TRIPPING-PLS-22-00037 | 2610/20220407/001 | Perlis | Perlis | 11kV | Underground | 07-04-2022 05:19 | PMU KANGAR CB4 | PMU KANGAR CB4 | PLB SM SAINS PERLIS KAN00706 - PDB MKTB PERGURUAN 2-KAN KAN00707 | Core Opened | Defective Manufacture | Cable | CABLE | 07-04-2022 05:37 | 07-04-2022 05:47 | 10 | 07-04-2022 23:16, 10-04-2022 11:58 | 10-04-2022 11:13, 10-04-2022 20:46 | 59, 8 | 10-04-2022 20:55 | 87.6
Northern | K1 | TRIPPING-PLS-22-00038 | 2610/20220407/027 | Perlis | Perlis | 11kV | Overhead | 07-04-2022 08:59 | PPU UNIMAP GIS 2K5 | PERLISPLANTATION KAN00237 | PDT MSM PERLIS - PBT SG. SERAI KAN00234 | Insulation Breakdown | Insulation Deterioration | Conductor | CABLE | 07-04-2022 09:00 | 07-04-2022 09:45 | 45 | 10-04-2022 11:17 | 10-04-2022 15:24 | 4 | 10-04-2022 15:44 | 78.75
Northern | K1 | TRIPPING-PLS-22-00039 | 2610/20220409/020 | Perlis | Perlis | 11kV | Underground | 09-04-2022 13:45 | PPU PADANG BESAR CB10 | PPU PADANG BESAR CB10 | CVIA CENTRE KAN03000 - PLB KUARI BATU REPUT KAN00092 | Insulation Burnt | Partly Environment | Cable Termination | CABLE | 09-04-2022 14:07 | 09-04-2022 14:39 | 32 | 12-04-2022 12:57 | 12-04-2022 18:43 | 5 | 12-04-2022 18:54 | 77.15
Northern | K1 | TRIPPING-KED-22-00175 | 0245/20220410/008 | Kedah | Kuala Nerang | 11kV | Overhead | 10-04-2022 11:31 | PPU KUALA NERANG 7K5 | A/R KG BELUKAR | PBT KG. KUBU KKN00268 - PBT KG. TANJUNG PUTUS KKN00270 | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 10-04-2022 11:45 | 10-04-2022 12:17 | 32 | 10-04-2022 17:07 | 11-04-2022 22:08 | 29 | 11-04-2022 22:37 | 35.1
Northern | K1 | TRIPPING-PLS-22-00040 | 2610/20220410/018 | Perlis | Perlis | 11kV | Overhead | 10-04-2022 13:39 | PPU PADANG BESAR CB2 | PDB GUA KELAM PEKAN KAKI BUKIT KAN00134 | PDB GUA KELAM PEKAN KAKI BUKIT KAN00134 - SJKC KONG HWA KAN02369 | Insulation Breakdown | Contamination | Cable Termination | CABLE | 10-04-2022 14:28 | 10-04-2022 15:13 | 45 | 10-04-2022 18:14 | 13-04-2022 23:21 | 77 | 13-04-2022 23:35 | 81.93
Northern | K1 | TRIPPING-KED-22-00177 | 0242/20220411/013 | Kedah | Jitra | 11kV | Underground | 11-04-2022 11:17 | PMU BUKIT KAYU HITAM BKH8 | STN SUIS ICQS KJT19258 CB1 | PATOD POS KAWALAN SEMPADAN KJT19168 - PDB KOMP BEBAS CUKAI KJT01107 | Insulation Burnt | Partly Environment | Cable Termination | OVERHEAD LINES | 11-04-2022 12:45 | 11-04-2022 13:10 | 25 | 12-04-2022 12:38 | 14-04-2022 12:59 | 48 | 14-04-2022 13:27 | 74.17
Northern | K1 | TRIPPING-PLS-22-00041 | 2610/20220415/023 | Perlis | Perlis | 11kV | Underground | 15-04-2022 17:13 | PPU BUKIT KETERI 7K5 | PDB TMN BESERI JAYA KAN00178 | PDB MRSM BESERI KAN00187 - LEMBAH BIAK KAN00188 | Core Opened | Defective Manufacture | Cable | CABLE | 15-04-2022 17:18 | 15-04-2022 17:51 | 33 | 15-04-2022 21:38 | 23-04-2022 21:17 | 191 | 23-04-2022 21:49 | 196.6
Northern | K1 | TRIPPING-KED-22-00194 | 0242/20220417/011 | Kedah | Jitra | 11kV | Overhead | 17-04-2022 00:53 | PPU DARULAMAN 4K5 | RUMAH KEDAI 50 UNIT KJT19305 | TMN KUBANGPASU - RUMAH KEDAI 50 UNIT KJT19305 | Snapped by Trees / Branches | Partly Environment | ABC Conductor | CABLE |  |  | 0 | 17-04-2022 11:58 | 18-04-2022 18:15 | 30 | 18-04-2022 18:29 | 41.6
Northern | K1 | TRIPPING-KED-22-00203 | 0242/20220419/035 | Kedah | Jitra | 11kV | Underground | 19-04-2022 20:34 | PPU CHANGLOON CL2 | PDB TMN MERBAU KJT18965 CB1 | PDB TMN SEMARAK API KJT01834 - PDB KG. TRADISI NO.2 KJT00870 | Core Opened | Defective Manufacture | Cable | CABLE | 19-04-2022 20:36 | 19-04-2022 21:16 | 40 | 19-04-2022 23:52 | 21-04-2022 11:03 | 35 | 21-04-2022 12:30 | 39.93
Northern | K1 | TRIPPING-PLS-22-00042 | 2610/20220423/002 | Perlis | Perlis | 11kV | Underground | 23-04-2022 09:14 | PPU SHORUBBER CB6 | PDB POLIKLINIK ARAU KAN00902 CB1 |  | Core Opened | Partly Environment | Cable | NO FAULT | 23-04-2022 09:15 |  | 0 |  |  |  | 23-04-2022 10:50 | 1.6
Northern | K1 | TRIPPING-KED-22-00213 | 0245/20220423/004 | Kedah | Kuala Nerang | 11kV | Underground | 23-04-2022 14:53 | A/R SEK MEN PEDU | A/R SEK MEN PEDU | PLB KG. TANJUNG LUAR KKN00143 - PAT KG. TONG PELU KKN00146 | Core Opened | Partly Environment | Cable | CABLE | 23-04-2022 15:22 | 23-04-2022 15:29 | 7 | 23-04-2022 16:36 | 25-04-2022 17:42 | 49 | 25-04-2022 17:45 | 50.87
Northern | K1 | TRIPPING-PLS-22-00043 | 2610/20220423/104 | Perlis | Perlis | 11kV | Underground | 23-04-2022 21:40 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 | PDB TMN UTARA JAYA KANGAR KAN00746 - PDB JPJ JEJAWI-VVIP KAN00747 | Insulation Failed, Shorted by Water Ingress | Under Investigation | Cable | CABLE | 23-04-2022 21:55 | 23-04-2022 22:19 | 24 | 24-04-2022 01:11 | 24-04-2022 01:24 | 0 | 24-04-2022 02:06 | 4.43
Northern | K1 | TRIPPING-PLS-22-00044 | 2610/20220424/001 | Perlis | Perlis | 11kV | Underground | 24-04-2022 00:20 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 | PDB TMN SEMATANG JAYA KAN00984 - PDB TMN UTARA JAYA KANGAR KAN00745 | Core Opened | Defective Manufacture | Cable | CABLE | 24-04-2022 00:21 | 24-04-2022 00:41 | 20 | 24-04-2022 21:45 | 26-04-2022 23:17 | 49 | 26-04-2022 23:40 | 71.33
Northern | K1 | TRIPPING-KED-22-00218 | 0242/20220425/033 | Kedah | Jitra | 11kV | Underground | 25-04-2022 09:39 | PPU CHANGLOON CL4 | S/S BLOK VALVE M2 KJT00720 CB1 | PAT BLOCK VALVE M2 - S/S BLOK VALVE M2 |  |  |  | CABLE | 25-04-2022 13:45 | 25-04-2022 14:15 | 30 | 25-04-2022 22:27 | 27-04-2022 18:06 | 43 | 27-04-2022 18:15 | 56.6
Northern | K1 | TRIPPING-PLS-22-00045 | 2610/20220425/026 | Perlis | Perlis | 11kV | Underground | 25-04-2022 14:17 | PMU KANGAR CB13 | PMU KANGAR CB13 | PMU KANGAR CB13 - PVCB SHOERUBBER KAN00738 | Core Opened | Partly Environment | Cable | CABLE |  |  | 0 | 27-04-2022 22:05 | 30-05-2022 20:27 | 790 | 31-05-2022 21:05 | 870.8
Northern | K1 | TRIPPING-PLS-22-00046 | 2610/20220425/033 | Perlis | Perlis | 11kV | Underground | 25-04-2022 14:36 | PMU KANGAR CB16 | PMU KANGAR CB16 | PMU KANGAR CB16 - PDB TMN SERI PULAI 3 KAN03053 | Core Opened | Partly Environment | Cable | CABLE | 25-04-2022 14:37 | 25-04-2022 15:00 | 23 | 27-04-2022 22:06 | 13-05-2022 06:16 | 368 | 13-05-2022 06:56 | 424.33
Northern | K1 | TRIPPING-PLS-22-00047 | 2610/20220430/001 | Perlis | Perlis | 11kV | Substation | 30-04-2022 00:57 | PPU BUKIT KETERI 7K5 | PDB TMN BESERI JAYA KAN00176 | PAT PADANG MELANGIT KAN00354 - | Insulation Failed and Shorted by Animal | Partly Environment | Cable Termination | TRANSIENT | 30-04-2022 00:54 | 30-04-2022 01:13 | 19 |  |  |  | 30-04-2022 02:22 | 1.42
Northern | K1 | TRIPPING-PLS-22-00048 | 2610/20220430/065 | Perlis | Perlis | 11kV | Underground | 30-04-2022 06:05 | PMU KANGAR CB14 | SSU KOMPLEKS PKENPS KAN03121 CB1 | PDB TMN KEMAJUAN 1 - PDB TMN KEMAJUAN 2 KAN00581 | Core Opened | Partly Environment | Cable | CABLE | 30-04-2022 06:16 | 30-04-2022 06:29 | 13 | 30-04-2022 21:50, 26-05-2022 21:24 | 11-05-2022 13:39, 27-05-2022 03:59 | 255, 6 | 27-05-2022 23:53 | 665.8
Northern | K1 | TRIPPING-PLS-22-00049 | 2610/20220502/166 | Perlis | Perlis | 11kV | Underground | 02-05-2022 09:25 | PPU PADANG BESAR CB9 | PDB TITI TINGGI KAN00091 CB1 | PBT BUKIT CABANG KAN02101 - PLB SMPG JALAN SAHABAT KAN02266 | Insulation Failed, Shorted by Water Ingress | Under Investigation | Cable | CABLE | 02-05-2022 09:36 | 02-05-2022 10:08 | 32 | 05-05-2022 22:01, 11-05-2022 13:41 | 11-05-2022 11:50, 11-05-2022 22:15 | 133, 8 | 11-05-2022 22:33 | 229.13
Northern | K1 | TRIPPING-KED-22-00240 | 0242/20220507/007 | Kedah | Jitra | 11kV | Overhead | 07-05-2022 08:56 | PMU TANJUNG PAUH TP9 | TMN DESA TANJUNG KJT19017 CB1 | KG NAGA - PDG GELAM | Loose and Opened | Partly Environment | Straight Through Joint | OVERHEAD LINES | 07-05-2022 09:22 | 07-05-2022 09:48 | 26 | 07-05-2022 21:33, 08-05-2022 22:09 | 08-05-2022 18:47, 09-05-2022 18:53 | 21, 20 | 09-05-2022 19:30 | 58.57
Northern | K1 | TRIPPING-KED-22-00249 | 0242/20220512/039 | Kedah | Jitra | 11kV | Underground | 12-05-2022 22:20 | PPU CHANGLOON CL2 | PLB SMPG BKT.TANGGA KJT00879 | QTRS UPP(KBG PASU) KJT01709 - BALAI BOMBA KJT00880 |  |  |  | CABLE | 12-05-2022 23:28 | 13-05-2022 00:02 | 34 | 13-05-2022 11:22 | 14-05-2022 17:46 | 30 | 14-05-2022 18:15 | 43.92
Northern | K1 | TRIPPING-PLS-22-00050 | 2610/20220514/002 | Perlis | Perlis | 11kV | Substation | 14-05-2022 06:06 | PPU SIMPANG EMPAT CB9 | PPU SIMPANG EMPAT CB9 | PAT PADANG BENTA KAN01222 - , - PDB SK SG. BEREMBANG KAN02302 - PAT TANJUNG GELAM KAN01161 | Dielectric breakdown | Shorted By Animal | HV Cable (Tx Tail) | SWITCHGEAR | 14-05-2022 06:10 | 14-05-2022 06:47 | 37 | 15-05-2022 00:55, 15-05-2022 16:06 | 15-05-2022 11:42, 16-05-2022 00:55 | 10, 8 | 16-05-2022 01:20 | 43.23
Northern | K1 | TRIPPING-PLS-22-00051 | 2610/20220514/025 | Perlis | Perlis | 11kV | Underground | 14-05-2022 07:14 | PPU BUKIT KETERI 7K5 | PDB TMN BESERI JAYA KAN00176 |  | Insulation Failed and Shorted by Animal | Partly Environment | HV Cable (Tx Tail) | NO FAULT |  | 14-05-2022 07:57 | 0 |  |  |  | 14-05-2022 10:00 | 2.77
Northern | K1 | TRIPPING-PLS-22-00052 | 2610/20220514/113 | Perlis | Perlis | 11kV | Underground | 14-05-2022 09:28 | PMU KUALA PERLIS CB1 | PMU KUALA PERLIS CB1 | PDB AMAN FISHMEAL KAN00624 - PDB PROCESSING FACTORY KAN00625 | Core Opened | Defective Manufacture | Cable | CABLE | 14-05-2022 09:29 | 14-05-2022 09:58 | 29 | 14-05-2022 22:21, 17-05-2022 10:44 | 15-05-2022 11:40, 17-05-2022 22:06 | 13, 11 | 18-05-2022 21:10 | 107.7
Northern | K1 | TRIPPING-KED-22-00259 | 0242/20220516/054 | Kedah | Jitra | 11kV | Underground | 16-05-2022 21:47 | PPU UUM SINTOK ST6 | PDB ASRAMA UUM KJT01743 | SS GENTING IBAI NO 2 KJT00808 - SSD RUMAH PAM GENTING IBAI KKN00596 | Core Broken | Partly Environment | Cable | CABLE | 16-05-2022 21:57 | 16-05-2022 22:33 | 36 | 17-05-2022 15:57 | 19-05-2022 01:49 | 33 | 19-05-2022 01:55 | 52.13
Northern | K1 | TRIPPING-PLS-22-00053 | 2610/20220520/010 | Perlis | Perlis | 11kV | Underground | 20-05-2022 09:40 | PPU PADANG BESAR CB2 | FISHING NET KAN03020 | PLB FELDA MATA AIR 1 KAN00086 - PLB FELDA MATA AIR 2 KAN02272 | Core Opened | Defective Manufacture | Cable | CABLE | 20-05-2022 09:50 | 20-05-2022 10:31 | 41 | 23-05-2022 21:20 | 24-05-2022 23:19 | 25 | 24-05-2022 23:38 | 109.97
Northern | K1 | TRIPPING-KED-22-00268 | 0245/20220520/005 | Kedah | Kuala Nerang | 11kV | Overhead | 20-05-2022 15:44 | PPU KUALA NERANG 9K5 | PPU KUALA NERANG 9K5 | PLB RMU PPU KUALA NERANG KKN00565 - PDB TMN AKASIA KKN00579 | Core Broken | Partly Environment | Cable | CABLE | 20-05-2022 15:48 | 20-05-2022 16:20 | 32 | 21-05-2022 00:23, 22-05-2022 16:06 | 22-05-2022 15:17, 23-05-2022 21:12 | 38, 29 | 23-05-2022 22:29 | 78.75
Northern | K1 | TRIPPING-PLS-22-00054 | 2610/20220522/014 | Perlis | Perlis | 11kV | Underground | 22-05-2022 17:28 | PPU SHORUBBER CB3 | PDB MIEL KUKUM JEJAWI KAN00731 CB1 | PDB IAMCO KAN00727 - ADVANCE CHICKEN KAN02351 | Core Opened | Defective Manufacture | Cable | CABLE | 22-05-2022 17:29 | 22-05-2022 17:50 | 21 | 22-05-2022 23:15, 05-06-2022 11:20 | 23-05-2022 20:51, 05-06-2022 18:54 | 21, 7 | 05-06-2022 19:15 | 337.78
Northern | K1 | TRIPPING-KED-22-00273 | 0245/20220522/028 | Kedah | Kuala Nerang | 11kV | Underground | 22-05-2022 23:09 | PPU KUALA NERANG 5K5 | A/R TG SEBERANG | PBT PADANG CENDERAI KKN00310 - PBT KG. LEMBAH GULA KKN00325 | Core Opened | Partly Environment | Cable | CABLE | 22-05-2022 23:40 | 22-05-2022 23:51 | 11 | 23-05-2022 12:51 | 23-05-2022 22:32 | 9 | 23-05-2022 23:10 | 24.02
Northern | K1 | TRIPPING-PLS-22-00055 | 2610/20220523/030 | Perlis | Perlis | 11kV | Underground | 23-05-2022 18:07 | PPU SIMPANG EMPAT CB7 | PPU SIMPANG EMPAT CB7 | PPU SIMPANG EMPAT CB7 - TMN PELANGI-KAN KAN01805 | Core Opened | Defective Manufacture | Cable | CABLE | 23-05-2022 18:08 | 23-05-2022 18:28 | 20 | 23-05-2022 23:32 | 06-06-2022 20:19 | 332 | 08-06-2022 13:14 | 379.12
Northern | K1 | TRIPPING-KED-22-00278 | 0242/20220525/001 | Kedah | Jitra | 11kV | Substation | 25-05-2022 02:08 | PPU KODIANG KD1 | PPU KODIANG KD1 | SSBT RUMAH PAM PERING KJT01634 - PLB KG. KANDIS KJT01147, SSBT RUMAH PAM PERING KJT01633 - | Dielectric | Dielectric Deterioration | RMU SF6 | CABLE | 25-05-2022 02:52 | 25-05-2022 03:22 | 30 | 26-05-2022 13:18, 27-05-2022 02:14 | 27-05-2022 08:58, 27-05-2022 09:01 | 19, 6 | 28-05-2022 18:18 | 88.17
Northern | K1 | TRIPPING-KED-22-00281 | 0245/20220525/012 | Kedah | Kuala Nerang | 11kV | Underground | 25-05-2022 12:56 | PPU KUALA NERANG 6K5 | PDB SMK KUALA NERANG KKN00054 |  | Core Opened | Partly Environment | Cable | NO FAULT | 25-05-2022 13:00 | 25-05-2022 13:34 | 34 |  |  |  | 25-05-2022 14:24 | 1.47
Northern | K1 | TRIPPING-KED-22-00285 | 0242/20220526/027 | Kedah | Jitra | 11kV | Underground | 26-05-2022 14:49 | PPU DARULAMAN 3K5 | PPU DARULAMAN 3K5 | PDB TMN BELIMBING NO.2 JITRA - PATOD KG. PENIA KJT00229 | Core Opened | Partly Environment | Cable | CABLE | 26-05-2022 14:55 | 26-05-2022 15:15 | 20 | 27-05-2022 22:53 | 29-05-2022 20:28 | 45 | 29-05-2022 21:48 | 78.98
Northern | K1 | TRIPPING-KED-22-00286 | 0242/20220526/047 | Kedah | Jitra | 11kV | Underground | 26-05-2022 17:08 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01798 CB1 | PBT KG. KUBANG PASU - KG JERAGAN | Core Opened | Partly Environment | Cable | CABLE | 26-05-2022 17:12 | 26-05-2022 17:25 | 13 | 27-05-2022 23:59 | 01-06-2022 20:13 | 116 | 02-06-2022 21:56 | 172.8
Northern | K1 | TRIPPING-PLS-22-00056 | 2610/20220529/005 | Perlis | Perlis | 11kV | Underground | 29-05-2022 03:08 | PPU PADANG BESAR CB10 | UKK PADANG BESAR KAN00047 CB1 | PBT CHECK POINT KAN00095 - PDB BATU BERTANGKUP KAN00096 | Core Opened | Defective Manufacture | Cable | CABLE | 29-05-2022 03:46 | 29-05-2022 04:40 | 54 | 31-05-2022 21:37, 14-06-2022 11:26 | 14-06-2022 09:31, 14-06-2022 22:36 | 323, 11 | 14-06-2022 23:40 | 404.53
Northern | K1 | TRIPPING-KED-22-00292 | 0242/20220530/089 | Kedah | Jitra | 11kV | Overhead | 30-05-2022 14:49 | PPU KODIANG KD2 | PPU KODIANG KD2 | PLB RUMAH PAM KODIANG KJT01244 - PATOD GUAR KHOR KJT01245 | Snapped by Trees / Branches | Partly Environment | ABC Conductor | CABLE | 30-05-2022 14:52 | 30-05-2022 15:36 | 44 | 30-05-2022 18:28 | 01-06-2022 21:26 | 50 | 01-06-2022 22:30 | 55.68
Northern | K1 | TRIPPING-KED-22-00299 | 0242/20220601/067 | Kedah | Jitra | 11kV | Underground | 01-06-2022 20:13 | PPU KODIANG KD6 | PPU KODIANG KD6 | PLB PEKAN KODIANG KJT01235 - PLB LPN KODIANG KJT01364 | Core Opened | Partly Environment | Cable | CABLE | 01-06-2022 20:15 | 01-06-2022 21:05 | 50 | 02-06-2022 22:51 | 06-06-2022 05:41 | 78 | 07-06-2022 11:20 | 135.12
Northern | K1 | TRIPPING-KED-22-00300 | 0242/20220602/035 | Kedah | Jitra | 11kV | Underground | 02-06-2022 11:01 | PMU BUKIT KAYU HITAM BKH4 | PMU BUKIT KAYU HITAM BKH4 | PDB TMN TEJA 1 KJT01615 - PDB PEKAN CHANGLUN 2 KJT00807 | Core Opened | Defective Manufacture | Cable | CABLE | 02-06-2022 11:05 | 02-06-2022 11:45 | 40 | 02-06-2022 18:31 | 07-06-2022 21:14 | 122 | 07-06-2022 22:20 | 131.32
Northern | K1 | TRIPPING-PLS-22-00057 | 2610/20220608/018 | Perlis | Perlis | 11kV | Underground | 08-06-2022 14:58 | PPU POLITEKNIK PAUH PERLIS 2 | PPU POLITEKNIK PAUH PERLIS CB2 | TMN KURUNG ANAI KAN02839 - FELDA LAKA SELATAN KJT00200 | Insulation Failed, Shorted by Water Ingress | Under Investigation | Cable | CABLE | 08-06-2022 15:05 | 08-06-2022 15:47 | 42 | 09-06-2022 23:43, 16-06-2022 21:59 | 10-06-2022 09:04, 17-06-2022 02:46 | 9, 4 | 17-06-2022 02:53 | 203.92
Northern | K1 | TRIPPING-PLS-22-00058 | 2610/20220609/035 | Perlis | Perlis | 11kV | Underground | 09-06-2022 19:22 | PMU CHUPING CB10 | PMU CHUPING CB10 | PMU CHUPING CB10 - PDB UITM ARAU KAN02053 | Core Opened | Partly Environment | Cable | CABLE | 09-06-2022 19:29 | 09-06-2022 19:32 | 3 | 09-06-2022 22:04, 23-06-2022 11:20 | 09-06-2022 23:41, 23-06-2022 21:33 | 1, 10 | 23-06-2022 22:07 | 338.75
Northern | K1 | TRIPPING-PLS-22-00059 | 2610/20220610/001 | Perlis | Perlis | 11kV | Underground | 10-06-2022 05:08 | PPU SHORUBBER CB4 | PVCB TMN JALI KAN02329 CB1 | PDB TMN KEMAJUAN 2 KAN00580 - PDB LPN KANGAR KAN00568 | Core Opened | Defective Manufacture | Cable | CABLE | 10-06-2022 05:10 | 10-06-2022 05:42 | 32 | 10-06-2022 21:42 | 22-06-2022 00:09 | 266 | 22-06-2022 00:22 | 283.23
Northern | K1 | TRIPPING-PLS-22-00060 | 2610/20220614/013 | Perlis | Perlis | 11kV | Underground | 14-06-2022 13:02 | PMU KANGAR CB10 | PDB FLAT POLIS KANGAR KAN00518 CB1 | PDB KOMP AGAMA ISLAM KAN00522 - PDB TMN TOK PELUKA KAN00537 | Core Opened | Defective Manufacture | Cable | CABLE | 14-06-2022 13:29 | 14-06-2022 13:57 | 28 | 21-06-2022 15:33 | 22-06-2022 00:32 | 8 | 22-06-2022 00:35 | 179.55
Northern | K1 | TRIPPING-KED-22-00327 | 0242/20220615/023 | Kedah | Jitra | 11kV | Substation | 15-06-2022 17:34 | PMU TANJUNG PAUH TP9 | TMN DESA TANJUNG KJT19017 | PBT PDG GELAM KJT00600 - PATOD KG. NAGA KJT00599 | Dielectric | Dielectric Deterioration | RMU SF6 | CABLE | 15-06-2022 18:06 | 15-06-2022 18:40 | 34 | 17-06-2022 16:04 | 18-06-2022 01:23 | 9 | 18-06-2022 02:25 | 56.85
Northern | K1 | TRIPPING-PLS-22-00061 | 2610/20220628/012 | Perlis | Perlis | 11kV | Underground | 28-06-2022 12:32 | PMU KUALA PERLIS CB1 | PLB TOK KUNING 1 KAN00614 CB1 | SMK SERIAB - PLB BEHOR TEMAK KAN00611 | Core Opened | Partly Environment | Cable | CABLE | 28-06-2022 14:28 | 28-06-2022 14:39 | 11 | 28-06-2022 17:03 | 02-07-2022 22:35 | 101 | 03-07-2022 08:07 | 115.58
Northern | K1 | TRIPPING-KED-22-00348 | 0242/20220628/026 | Kedah | Jitra | 11kV | Underground | 28-06-2022 19:25 | PPU KODIANG KD2 | PDB SM TUNKU BENDAHARA KJT01255 CB1 | PAT GUAR BATU HITAM KJT01272 - PLD FELDA BATU 8 CHANGLUN KJT19117 | Core Opened | Partly Environment | Cable | CABLE | 28-06-2022 19:26 | 28-06-2022 20:00 | 34 | 28-06-2022 23:44 | 08-07-2022 10:56 | 227 | 08-07-2022 11:30 | 232.08
Northern | K1 | TRIPPING-KED-22-00349 | 0242/20220628/060 | Kedah | Jitra | 11kV | Underground | 28-06-2022 23:34 | PPU JERLUN SJ4 | PPU JERLUN SJ4 | PBT KEMBOJA KJT01530 - PAT KG. PMTG BONGLAI KECIL KJT01531 | Core Opened | Partly Environment | Cable | CABLE | 28-06-2022 23:59 | 29-06-2022 00:25 | 26 | 29-06-2022 20:45 | 30-06-2022 16:29 | 19 | 30-06-2022 17:05 | 41.52
Northern | K1 | TRIPPING-PLS-22-00062 | 2610/20220702/002 | Perlis | Perlis | 11kV | Overhead | 02-07-2022 06:33 | PMU KUALA PERLIS CB2 | PMU KUALA PERLIS CB2 | PMU KUALA PERLIS CB2 - TMN BUNGA PADI KAN01854 | Snapped by Trees / Branches | Partly Environment | ABC Conductor | OVERHEAD LINES | 02-07-2022 06:49 | 02-07-2022 07:03 | 14 | 02-07-2022 21:26 | 04-07-2022 21:44 | 48 | 04-07-2022 21:54 | 63.35
Northern | K1 | TRIPPING-KED-22-00359 | 0242/20220703/050 | Kedah | Jitra | 11kV | Underground | 03-07-2022 15:30 | PPU JERLUN SJ6 | PPU JERLUN SJ6 | PBT PIDA 5 PMTG BONGLAI KJT01500 - PATOD SEMATANG JAWA KJT01501 | Dielectric breakdown | Dielectric Deterioration | Cable Termination | CABLE | 03-07-2022 15:35 | 03-07-2022 16:14 | 39 | 04-07-2022 12:54 | 05-07-2022 19:03 | 30 | 05-07-2022 19:49 | 52.32
Northern | K1 | TRIPPING-KED-22-00363 | 0245/20220705/005 | Kedah | Kuala Nerang | 11kV | Underground | 05-07-2022 09:50 | PPU MINI PPU L/AIR PDG SANAI LA3 | PPU MINI PPU L/AIR PDG SANAI LA3 | PDB LOJI AIR PADANG SANAI - LDG SG SERAYA KKN00772 | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | OVERHEAD LINES | 05-07-2022 09:54 | 05-07-2022 10:30 | 36 | 05-07-2022 18:58 | 05-07-2022 22:23 | 3 | 05-07-2022 22:42 | 12.87
Northern | K1 | TRIPPING-KED-22-00370 | 0242/20220708/023 | Kedah | Jitra | 11kV | Overhead | 08-07-2022 18:20 | PPU KODIANG KD1 | SSBT RUMAH PAM PERING KJT01634 | PBT KG. ALOR JANGGUS KJT01193 - PLD FELDA BATU 8 CHANGLUN KJT19118 | Snapped by Trees / Branches | Partly Environment | ABC Conductor | CABLE | 08-07-2022 18:32 | 08-07-2022 18:50 | 18 | 08-07-2022 23:27, 09-07-2022 16:18 | 09-07-2022 11:52, 09-07-2022 18:53 | 12, 2 | 09-07-2022 19:20 | 25
Northern | K1 | TRIPPING-KED-22-00371 | 0245/20220709/001 | Kedah | Kuala Nerang | 11kV | Overhead | 09-07-2022 07:04 | PPU KUALA NERANG 6K5 | PPU KUALA NERANG 6K5 |  | Insulation Failed, Shorted by Water Ingress | Poor Workmanship | Cable Termination | NO FAULT | 09-07-2022 07:37 | 09-07-2022 07:47 | 10 | 09-07-2022 08:22 | 09-07-2022 08:36 | 0 | 09-07-2022 09:24 | 2.33
Northern | K1 | TRIPPING-PLS-22-00063 | 2610/20220710/018 | Perlis | Perlis | 11kV | Underground | 10-07-2022 07:09 | PMU KANGAR CB1 | VCB MAHKAMAH TINGGI PERLIS KAN00445 CB1 | PDB DEWAN WARISAN - COMP-SUB DEWAN MB-VVIP KAN00447 |  |  |  | CABLE | 10-07-2022 09:10 | 15-07-2022 09:25 | 7215 | 10-07-2022 09:58, 10-07-2022 23:21, 30-07-2022 10:49 | 10-07-2022 10:06, 12-07-2022 12:22, 30-07-2022 21:57 | 0, 37, 11 | 30-07-2022 22:15 | 495.1
Northern | K1 | TRIPPING-KED-22-00374 | 0242/20220710/084 | Kedah | Jitra | 11kV | Substation | 10-07-2022 21:10 | PPU JERLUN SJ4 | PDB KLG BERAS SUPREME KJT01676 |  | Incoming Termination - Burnt Marks | Partly Environment | HV Cable (Tx Tail) | NO FAULT | 10-07-2022 21:12 | 10-07-2022 21:55 | 43 |  |  |  | 10-07-2022 22:12 | 1.03
Northern | K1 | TRIPPING-PLS-22-00064 | 2610/20220712/004 | Perlis | Perlis | 11kV | Underground | 12-07-2022 02:58 | PMU KANGAR CB16 | SSU GIANT KGAR KAN02771 CB1 | HTL SRI MALAYSIA KANGAR KAN02047 - SSU SUK N.PERLIS KAN03137 | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 12-07-2022 04:00 | 12-07-2022 04:30 | 30 | 13-07-2022 18:50 | 17-07-2022 18:08 | 95 | 17-07-2022 18:26 | 135.47
Northern | K1 | TRIPPING-PLS-22-00065 | 2610/20220715/023 | Perlis | Perlis | 11kV | Underground | 15-07-2022 15:42 | PPU PADANG BESAR CB2 | PDB GUA KELAM PEKAN KAKI BUKIT KAN00134 |  | Core Opened | Partly Environment | Cable | TRANSIENT | 15-07-2022 16:05 | 15-07-2022 16:30 | 25 |  |  |  | 15-07-2022 18:03 | 2.35
Northern | K1 | TRIPPING-KED-22-00390 | 0242/20220717/013 | Kedah | Jitra | 11kV | Underground | 17-07-2022 13:19 | PPU JERLUN SJ4 | PPU JERLUN SJ4 | PBT KEMBOJA KJT01530 - PAT KG. PMTG BONGLAI KECIL KJT01531 | Core Opened | Defective Manufacture | Cable | CABLE | 17-07-2022 13:20 | 17-07-2022 14:02 | 42 | 17-07-2022 21:00 | 20-07-2022 14:27 | 65 | 20-07-2022 15:20 | 74.02
Northern | K1 | TRIPPING-PLS-22-00066 | 2610/20220719/014 | Perlis | Perlis | 11kV | Overhead | 19-07-2022 14:50 | PPU BUKIT KETERI 7K5 | PPU BUKIT KETERI 7K5 | PPU BUKIT KETERI 7K5 - PDB TMN BESERI JAYA KAN00177 | Snapped by Trees / Branches | Partly Environment | ABC Conductor | CABLE | 19-07-2022 14:57 | 19-07-2022 15:32 | 35 | 19-07-2022 21:32 | 24-07-2022 00:12 | 98 | 24-07-2022 00:21 | 105.52
Northern | K1 | TRIPPING-PLS-22-00067 | 2610/20220721/002 | Perlis | Perlis | 11kV | Substation | 21-07-2022 03:36 | PPU SIMPANG EMPAT CB9 | PPU SIMPANG EMPAT CB9 | PAT KG. PULAU-VVIP KAN01224 - | Insulation Damaged, Shorted by Animal | Partly Environment | HV Cable (Tx Tail) | TRANSIENT | 21-07-2022 03:56 | 21-07-2022 04:29 | 33 |  |  |  | 21-07-2022 05:17 | 1.68
Northern | K1 | TRIPPING-KED-22-00404 | 0242/20220721/025 | Kedah | Jitra | 11kV | Substation | 21-07-2022 12:50 | PMU BUKIT KAYU HITAM BKH4 | PMU BUKIT KAYU HITAM BKH4 | PMU BUKIT KAYU HITAM BKH4 - PDB PLUSWAY KJT01132 | Dielectric | Dielectric Deterioration | RMU SF6 | CABLE | 21-07-2022 13:15 | 21-07-2022 14:00 | 45 | 22-07-2022 01:23 | 22-07-2022 02:22 | 0 | 24-07-2022 11:16 | 70.43
Northern | K1 | TRIPPING-KED-22-00408 | 0242/20220721/115 | Kedah | Jitra | 11kV | Underground | 21-07-2022 19:25 | PPU JERLUN SJ6 | PPU JERLUN SJ6 | PLB PIDA 3 TUNJANG KJT01519 - SMK PMTG.BONGLAI KJT01518 | Core Opened | Partly Environment | Cable | CABLE | 21-07-2022 19:27 | 21-07-2022 19:40 | 13 | 22-07-2022 20:32 | 24-07-2022 17:37 | 45 | 24-07-2022 18:30 | 71.08
Northern | K1 | TRIPPING-KED-22-00410 | 0245/20220722/001 | Kedah | Kuala Nerang | 11kV | Underground | 22-07-2022 03:47 | PPU KUALA NERANG 6K5 | PDB SMK KUALA NERANG KKN00054 | PLB BATU 19 KNG KKN00705 - | Core Opened | Defective Manufacture | Cable | TRANSIENT | 22-07-2022 03:58 | 22-07-2022 04:17 | 19 |  |  |  | 22-07-2022 05:15 | 1.47
Northern | K1 | TRIPPING-PLS-22-00068 | 2610/20220722/005 | Perlis | Perlis | 11kV | Underground | 22-07-2022 10:12 | PPU SHORUBBER CB2 | PDB ALOR LANCANG KAN00837 CB1 | TMN GUAR HALBAN - P/E C/SUB SK ORAN KAN02482 | Core Opened | Partly Environment | Cable | CABLE | 22-07-2022 10:18 | 22-07-2022 10:37 | 19 | 22-07-2022 22:37 | 26-07-2022 13:07 | 86 | 26-07-2022 13:10 | 98.97
Northern | K1 | TRIPPING-PLS-22-00069 | 2610/20220722/042 | Perlis | Perlis | 11kV | Underground | 22-07-2022 19:03 | PPU SHORUBBER CB5 | BEHOR MENTALOON KAN00975 CB1 | PLB CEMUMAR TAMBUN TULANG(NOP) KAN01004 - SK RAJA(P) BUDRIAH-VVIP KAN02308 | Core Opened | Defective Manufacture | Cable | OVERHEAD LINES | 22-07-2022 19:06 | 22-07-2022 19:36 | 30 |  |  |  | 22-07-2022 22:15 | 3.2
Northern | K1 | TRIPPING-PLS-22-00070 | 2610/20220724/017 | Perlis | Perlis | 11kV | Underground | 24-07-2022 17:16 | PPU SIMPANG EMPAT CB7 | PPU SIMPANG EMPAT CB7 | PPU SIMPANG EMPAT CB7 - TMN PELANGI-KAN KAN01805 | Core Opened | Partly Environment | Cable | CABLE | 24-07-2022 17:18 | 24-07-2022 18:00 | 42 | 24-07-2022 21:55, 22-08-2022 22:37 | 06-08-2022 21:34, 19-10-2022 18:31 | 311, 1387 | 19-10-2022 19:07 | 2089.85
Northern | K1 | TRIPPING-KED-22-00420 | 0242/20220726/025 | Kedah | Jitra | 11kV | Underground | 26-07-2022 11:43 | PPU PELUBANG PL3 | PDB SK PENGHULU HJ DARUS KJT00700 CB1 | PAT KG. CEROK LATAH KJT00706 - R/PAM LEMBAH ARANG KJT19280 | Core Opened | Partly Environment | Cable | CABLE | 26-07-2022 11:46 | 26-07-2022 12:19 | 33 | 26-07-2022 23:14 | 27-07-2022 18:16 | 19 | 27-07-2022 18:40 | 30.95
Northern | K1 | TRIPPING-PLS-22-00071 | 2610/20220728/018 | Perlis | Perlis | 11kV | Underground | 28-07-2022 09:07 | PMU KUALA PERLIS CB5 | PMU KUALA PERLIS CB5 | PLB LOT 764 TMN KUALA PERLIS KAN01181 - KLG AIS IGLOO KAN02065 | Core Opened | Partly Environment | Cable | CABLE | 28-07-2022 09:09 | 28-07-2022 09:35 | 26 | 29-07-2022 21:35 | 21-08-2022 18:22 | 548 | 22-08-2022 21:06 | 611.98
Northern | K1 | TRIPPING-KED-22-00442 | 0242/20220801/013 | Kedah | Jitra | 11kV | Underground | 01-08-2022 12:07 | PPU KODIANG KD1 | A/R CEROK MOKAM 1 Bay AR | PDB KLG BAJA MK HOSBA KJT01692 - PDT YUNG HENG POULTRY KJT19442 | Core Opened | Partly Environment | Cable | OVERHEAD LINES | 01-08-2022 13:57 | 01-08-2022 14:31 | 34 | 02-08-2022 23:39 | 03-08-2022 18:01 | 18 | 03-08-2022 18:34 | 54.45
Northern | K1 | TRIPPING-PLS-22-00072 | 2610/20220802/012 | Perlis | Perlis | 11kV | Underground | 02-08-2022 15:09 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 | PDB TMN UTARA JAYA KANGAR KAN00744 - PDB SHOERUBBER LAMA KAN00743 | Insulation Failed, Shorted by Corrosive Evmnt | Partly Environment | Cable Termination | CABLE | 02-08-2022 15:10 | 02-08-2022 15:26 | 16 | 11-08-2022 16:27 | 12-08-2022 04:03 | 11 | 12-08-2022 04:08 | 228.98
Northern | K1 | TRIPPING-PLS-22-00073 | 2610/20220803/002 | Perlis | Perlis | 11kV | Underground | 03-08-2022 08:09 | PPU MINI PPU ABI CB13 | PPU MINI PPU ABI CB13 | PDB TMN MAS MUDA KAN02024 - PBT KG TELOK JAMBU KAN00394 | Core Opened | Partly Environment | Cable | CABLE | 03-08-2022 08:30 | 03-08-2022 08:58 | 28 | 04-08-2022 20:37 | 10-08-2022 02:59 | 126 | 10-08-2022 03:16 | 163.12
Northern | K1 | TRIPPING-PLS-22-00074 | 2610/20220805/003 | Perlis | Perlis | 11kV | Underground | 05-08-2022 01:14 | PPU SHORUBBER CB4 | PVCB TMN JALI KAN02329 CB1 | PDB TMN KEMAJUAN 1 KAN00582 - PDB TMN KEMAJUAN 2 KAN00581 | Core Opened | Partly Environment | Cable | CABLE | 05-08-2022 01:15 | 05-08-2022 01:40 | 25 | 06-08-2022 21:40 | 17-08-2022 13:56 | 256 | 17-08-2022 14:07 | 300.88
Northern | K1 | TRIPPING-KED-22-00462 | 0242/20220807/027 | Kedah | Jitra | 11kV | Underground | 07-08-2022 16:25 | PPU CHANGLOON CL6 | PDB KOMP CHANGLUN 2 KJT00802 CB1 | PATOD BATU 25 KJT00815 - PLB INTER CHANGE KJT00814 | Core Opened | Partly Environment | Cable | CABLE | 07-08-2022 16:27 | 07-08-2022 17:10 | 43 | 07-08-2022 19:49, 08-08-2022 00:05 | 07-08-2022 20:32, 11-08-2022 16:58 | 0, 88 | 11-08-2022 17:42 | 97.28
Northern | K1 | TRIPPING-KED-22-00470 | 0245/20220812/002 | Kedah | Kuala Nerang | 11kV | Overhead | 12-08-2022 07:31 | PPU NAKA 1K5 | PPU NAKA 1K5 | PLB REBAN AYAM PONG KKN03050 - PDB INDUSTRI KEDA NAKA KKN00614, - PDB INDUSTRI KEDA NAKA KKN00405 - PBT KEDA NAKA KKN00398 | Insulation Failed, Shorted by Old External Damage | Partly Environment | Cable | CABLE, CABLE | 12-08-2022 08:07 | 12-08-2022 08:41 | 34 | 12-08-2022 17:17, 12-08-2022 17:20 | 17-08-2022 18:57, 14-08-2022 21:59 | 121, 52 | 17-08-2022 20:15 | 132.73
Northern | K1 | TRIPPING-PLS-22-00075 | RE/2610/20220812/PLS/00075 | Perlis | Perlis | 11kV | Underground | 12-08-2022 12:38 | PPU PADANG BESAR CB16 | PPU PADANG BESAR CB16 |  |  |  |  | NO FAULT | 12-08-2022 12:57 | 12-08-2022 14:40 | 103 |  |  |  | 12-08-2022 17:43 | 5.08
Northern | K1 | TRIPPING-KED-22-00473 | 0242/20220814/001 | Kedah | Jitra | 11kV | Underground | 14-08-2022 00:05 | PPU UUM SINTOK ST3 | PPU UUM SINTOK ST3 | PDB SM REN JALAN SINTOK KJT01013 - PDT RUMAH PAM ASRAMA UUM KJT01014 | Insulation Burnt | Partly Environment | Cable Termination | CABLE, SWITCHGEAR | 14-08-2022 00:14 | 14-08-2022 00:55 | 41 | 14-08-2022 15:19, 15-08-2022 16:46 | 15-08-2022 16:44, 16-08-2022 06:49 | 25, 14 | 16-08-2022 07:43 | 55.63
Northern | K1 | TRIPPING-KED-22-00475 | 0242/20220814/006 | Kedah | Jitra | 11kV | Underground | 14-08-2022 01:59 | PPU KODIANG KD2 | PPU KODIANG KD2 | PLB RUMAH PAM KODIANG KJT01250 - PDB SM TUNKU BENDAHARA KJT01251 | Core Opened | Partly Environment | Cable | CABLE | 14-08-2022 02:17 | 14-08-2022 02:35 | 18 | 14-08-2022 15:20 | 18-08-2022 10:59 | 91 | 18-08-2022 15:05 | 109.1
Northern | K1 | TRIPPING-KED-22-00483 | 0242/20220816/018 | Kedah | Jitra | 11kV | Underground | 16-08-2022 10:21 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01798 CB1 | PBT KG. JERAGAN KJT00730 - PBT KG. KUBANG PASU KJT00729 | Insulation Failed, Shorted by Water Ingress | Partly Environment | Cable | CABLE | 16-08-2022 10:29 | 16-08-2022 11:08 | 39 | 16-08-2022 21:21 | 18-08-2022 12:06 | 38 | 20-08-2022 15:42 | 101.35
Northern | K1 | TRIPPING-PLS-22-00076 | 2610/20220817/009 | Perlis | Perlis | 11kV | Underground | 17-08-2022 11:48 | PMU KUALA PERLIS CB7 | PMU KUALA PERLIS CB7 | PMU KUALA PERLIS CB7 - PDB PERLIS MARINE KAN00650 | Insulation Failed, Shorted by Water Ingress | Under Investigation | Cable | CABLE | 17-08-2022 11:59 | 17-08-2022 12:17 | 18 | 17-08-2022 21:26 | 14-09-2022 01:52 | 652 | 14-09-2022 02:15 | 662.45
Northern | K1 | TRIPPING-KED-22-00491 | 0245/20220818/011 | Kedah | Kuala Nerang | 11kV | Underground | 18-08-2022 19:36 | PPU NAKA 4K5 | PPU NAKA 4K5 | PADAT KLINIK KESIHATAN NAKA KKN00734 - PDB BDR BARU NAKA KKN00373 | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 18-08-2022 19:51 | 18-08-2022 20:26 | 35 | 18-08-2022 22:22 | 21-08-2022 21:31 | 71 | 21-08-2022 21:58 | 74.37
Northern | K1 | TRIPPING-KED-22-00492 | 0242/20220819/014 | Kedah | Jitra | 11kV | Underground | 19-08-2022 14:33 | PPU UUM SINTOK ST5 | PPU UUM SINTOK ST5 | PPU UUM SINTOK ST5 - PLB RUMAH PAM MARDI-JITRA KJT01051 | Insulation Burnt | Partly Environment | Cable Termination | CABLE | 19-08-2022 14:36 | 19-08-2022 15:10 | 34 | 20-08-2022 12:43 | 20-08-2022 16:36 | 3 | 20-08-2022 18:09 | 27.6
Northern | K1 | TRIPPING-KED-22-00496 | 0242/20220821/010 | Kedah | Jitra | 11kV | Underground | 21-08-2022 07:54 | PPU JERLUN SJ6 | PPU JERLUN SJ6 |  | Shorted by Animal | Partly Environment | Transformer Bushing | TRANSIENT | 21-08-2022 07:56 | 21-08-2022 08:40 | 44 | 21-08-2022 16:03 | 21-08-2022 16:37 | 0 | 21-08-2022 16:53 | 8.98
Northern | K1 | TRIPPING-PLS-22-00077 | 2610/20220822/048 | Perlis | Perlis | 11kV | Underground | 22-08-2022 22:12 | PPU MINI PPU ABI CB11 | PPU MINI PPU ABI CB11 | KUARI BATU DAYALAM - PLB SMPG KURUNG BATANG KAN00344 | Core Opened | Partly Environment | Cable | CABLE | 22-08-2022 22:25 | 22-08-2022 23:09 | 44 | 23-08-2022 19:31, 14-09-2022 15:25 | 08-09-2022 17:53, 15-09-2022 14:07 | 382, 22 | 15-09-2022 14:20 | 568.13
Northern | K1 | TRIPPING-PLS-22-00078 | 2610/20220830/005 | Perlis | Perlis | 11kV | Underground | 30-08-2022 10:59 | PMU CHUPING CB6 | PMU CHUPING CB6 | PDB KOK KELANG 2 KAN00250 - FELDA CHUPING NO.2 KAN02698 | Core Opened | Partly Environment | Cable | CABLE | 30-08-2022 11:01 | 30-08-2022 11:30 | 29 | 31-08-2022 03:15 | 07-09-2022 22:47 | 187 | 07-09-2022 23:29 | 204.5
Northern | K1 | TRIPPING-PLS-22-00079 | 2610/20220831/002 | Perlis | Perlis | 11kV | Underground | 31-08-2022 02:49 | PMU KUALA PERLIS CB2 | TMN BUNGA PADI KAN00386 CB1 | TMN BINTONG CERIA KAN02790 - PDB PADANG KATONG-VVIP -RB17 KAN00383 | Insulation Failed, Shorted by Water Ingress | Under Investigation | Cable | CABLE | 31-08-2022 03:01 | 31-08-2022 03:30 | 29 | 08-09-2022 10:15 | 08-09-2022 23:36 | 13 | 08-09-2022 00:18 | 189.48
Northern | K1 | TRIPPING-KED-22-00516 | 0242/20220831/036 | Kedah | Jitra | 11kV | Underground | 31-08-2022 22:58 | PPU CHANGLOON CL2 | PDB TMN MERBAU KJT01859 CB1 | PDB KG. TITI KERBAU KJT00847 - PATOD KG. BARU KJT00848 | Core Opened | Partly Environment | Cable | CABLE | 31-08-2022 23:00 | 31-08-2022 23:30 | 30 | 01-09-2022 16:05 | 04-09-2022 22:18 | 78 | 04-09-2022 23:10 | 96.2
Northern | K1 | TRIPPING-PLS-22-00080 | 2610/20220902/007 | Perlis | Perlis | 11kV | Underground | 02-09-2022 12:50 | PPU SIMPANG EMPAT CB1 | PDB KLG PADI MAJU KAN01040 CB1 | PAT CHE OK LUAR KAN01019 - PBT KG. CEMUMAR DLM KAN01014 | Core Opened | Defective Manufacture | Cable | CABLE | 02-09-2022 12:53 | 02-09-2022 13:30 | 37 | 08-09-2022 17:58 | 08-09-2022 21:59 | 4 | 08-09-2022 22:35 | 153.75
Northern | K1 | TRIPPING-KED-22-00523 | 0242/20220904/020 | Kedah | Jitra | 11kV | Underground | 04-09-2022 17:25 | PMU TANJUNG PAUH TP21 | PMU TANJUNG PAUH TP21 | PDB R/KEDAI 22 UNIT(NOP)-RMU A - PMU TANJUNG PAUH TP21 | Core Opened | Defective Manufacture | Cable | CABLE | 04-09-2022 17:27 | 04-09-2022 18:12 | 45 | 04-09-2022 23:52 | 08-09-2022 16:13 | 88 | 08-09-2022 17:50 | 96.42
Northern | K1 | TRIPPING-PLS-22-00081 | 2610/20220910/028 | Perlis | Perlis | 11kV | Underground | 10-09-2022 19:52 | PPU LOJI AIR ARAU GIS 4K5 | PPU LOJI AIR ARAU GIS 4K5 | PPU LOJI AIR ARAU GIS 4K5 - PBT KG. SENA KAN01878 | Core Opened | Partly Environment | Cable | CABLE | 10-09-2022 20:07 | 10-09-2022 20:36 | 29 | 11-09-2022 20:39 | 17-09-2022 17:28 | 140 | 17-09-2022 18:04 | 166.2
Northern | K1 | TRIPPING-PLS-22-00082 | 2610/20220917/003 | Perlis | Perlis | 11kV | Underground | 17-09-2022 03:11 | PPU MINI PPU ABI CB11 | PPU MINI PPU ABI CB11 | PAT SMPG SG SIRAN KAN00348 - | Core Opened | Partly Environment | Cable | TRANSIENT | 17-09-2022 04:12 | 17-09-2022 04:21 | 9 |  |  |  | 17-09-2022 04:40 | 1.48
Northern | K1 | TRIPPING-KED-22-00551 | 0242/20220917/019 | Kedah | Jitra | 11kV | Underground | 17-09-2022 17:10 | PPU DARULAMAN 4K5 | RUMAH KEDAI 50 UNIT KJT19301 CB1 | PDB KLINIK KESIHATAN TUNJANG KJT01739 - PLB TUNJANG KJT00079 | Core Opened | Defective Manufacture | Cable | CABLE | 17-09-2022 17:13 | 17-09-2022 17:42 | 29 | 17-09-2022 22:02 | 18-09-2022 19:45 | 21 | 18-09-2022 20:45 | 27.58
Northern | K1 | TRIPPING-KED-22-00552 | 0242/20220917/082 | Kedah | Jitra | 11kV | Underground | 17-09-2022 21:39 | PPU KODIANG KD1 | A/R CEROK MOKAM 1 Bay AR | PAT CEROK MOKAM 2 KJT01218 - | Core Opened | Defective Manufacture | Cable | TRANSIENT | 17-09-2022 21:43 | 17-09-2022 21:45 | 2 |  |  |  | 17-09-2022 23:35 | 1.93
Northern | K1 | TRIPPING-KED-22-00561 | 0245/20220921/011 | Kedah | Kuala Nerang | 11kV | Overhead | 21-09-2022 13:43 | PPU KUALA NERANG 6K5 | PDB SMK KUALA NERANG KKN00054 | PBT KUALA PAI - SSL KUALA PAI KJT18891 | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 21-09-2022 13:57 | 21-09-2022 14:34 | 37 | 21-09-2022 18:11 | 22-09-2022 20:44 | 26 | 22-09-2022 20:50 | 31.12
Northern | K1 | TRIPPING-PLS-22-00083 | 2610/20220923/001 | Perlis | Perlis | 11kV | Substation | 23-09-2022 01:41 | PMU KUALA PERLIS CB1 | PDB AMAN FISHMEAL KAN00623 CB1 |  | Insulation Failed and Shorted by Animal | Partly Environment | HV Cable (Tx Tail) | TRANSIENT | 23-09-2022 01:43 | 23-09-2022 02:25 | 42 |  |  |  | 23-09-2022 03:22 | 1.68
Northern | K1 | TRIPPING-KED-22-00574 | 0242/20220926/011 | Kedah | Jitra | 11kV | Underground | 26-09-2022 05:41 | PMU TANJUNG PAUH TP14 | PMU TANJUNG PAUH TP14 | PDB ASRAMA IPDA - PDB BANGLO NO.2-VVIP KJT00195 | Core Opened | Partly Environment | Cable | CABLE | 26-09-2022 05:50 |  | 0 | 26-09-2022 22:25 | 29-09-2022 21:36 | 71 | 29-09-2022 22:10 | 88.48
Northern | K1 | TRIPPING-PLS-22-00085 | 2610/20220926/018 | Perlis | Perlis | 11kV | Substation | 26-09-2022 12:24 | PPU SIMPANG EMPAT CB6 | PPU SIMPANG EMPAT CB6 | PDB TMN BUMITA KAN00595 - PDB SM SYED ALWI KAN00673 | Cable Compartment - Termination Fault | Partly Environment | Circuit Breaker | CABLE | 26-09-2022 12:27 | 26-09-2022 12:50 | 23 | 03-10-2022 11:09 | 03-10-2022 21:51 | 10 | 03-10-2022 22:04 | 177.67
Northern | K1 | TRIPPING-PLS-22-00086 | 2610/20220930/019 | Perlis | Perlis | 11kV | Underground | 30-09-2022 19:59 | PPU PADANG BESAR CB7 | PVCB QTRS KTMB KAN02216 CB1 | PDB DEPOH 2-KAN KAN02508 - DEPOT KTMB PADANG BESAR KAN01962 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 30-09-2022 20:02 | 30-09-2022 20:45 | 43 | 02-10-2022 20:34 | 02-10-2022 23:26 | 2 | 03-10-2022 23:24 | 75.42
Northern | K1 | TRIPPING-PLS-22-00087 | 2610/20221002/004 | Perlis | Perlis | 11kV | Underground | 02-10-2022 03:44 | PPU SIMPANG EMPAT CB5 | SEK MEN SANGLANG KAN01095 CB1 | PDB K/UDANG RAMADIN KAN01130 - PDB KOLAM UDANG YAYASAN ISLAM KAN01131 | Core Opened | Partly Environment | Cable | CABLE | 02-10-2022 03:45 | 02-10-2022 04:20 | 35 | 03-10-2022 01:59 | 05-10-2022 22:26 | 68 | 05-10-2022 22:30 | 90.77
Northern | K1 | TRIPPING-KED-22-00593 | 0242/20221004/018 | Kedah | Jitra | 11kV | Underground | 04-10-2022 10:30 | PPU DARULAMAN 10K5 | STN SUIS 11KV IKBN JITRA KJT18896 CB1 | PDB KLG BERAS CHEM KJT00941 - P/E POULTRY FARM KJT19039 | Core Opened | Partly Environment | Cable | CABLE | 04-10-2022 10:35 | 04-10-2022 11:15 | 40 | 04-10-2022 17:08 | 06-10-2022 19:07 | 49 | 06-10-2022 19:20 | 56.83
Northern | K1 | TRIPPING-PLS-22-00088 | 2610/20221004/012 | Perlis | Perlis | 11kV | Underground | 04-10-2022 11:06 | PMU KUALA PERLIS CB3 | PMU KUALA PERLIS CB3 | PAT KURONG TENGAH KAN02582 - PDB BERNAS PADANG JAMIL KAN01214 | Core Opened | Partly Environment | Cable | CABLE | 04-10-2022 11:07 | 04-10-2022 11:22 | 15 | 07-10-2022 16:20 | 08-10-2022 23:22 | 31 | 08-10-2022 23:30 | 108.4
Northern | K1 | TRIPPING-KED-22-00592 | 0242/20221004/034 | Kedah | Jitra | 11kV | Underground | 04-10-2022 11:52 | PPU PELUBANG PL3 | PDB SK PENGHULU HJ DARUS KJT00700 CB1 | PBT KG. LEMBAH ARANG KJT18894 - SSL KUALA PAI KJT18893 | Insulation Failed, Shorted by Corrosive Evmnt | Partly Environment | Cable Termination | CABLE | 04-10-2022 11:53 | 04-10-2022 12:25 | 32 | 04-10-2022 17:11 | 10-10-2022 17:57 | 144 | 10-10-2022 18:11 | 150.32
Northern | K1 | TRIPPING-PLS-22-00089 | 2610/20221005/016 | Perlis | Perlis | 11kV | Underground | 05-10-2022 15:04 | PMU KANGAR CB7 | TMN BUNGA PADI KAN00388 CB1 | PAT WANG KENOI KAN00409 - PDB TMN SRI BINTONG MAJU KAN02246 | Core Opened | Partly Environment | Cable | CABLE | 05-10-2022 15:06 |  | 0 | 10-10-2022 15:52 | 10-10-2022 22:48 | 6 | 10-10-2022 23:43 | 128.65
Northern | K1 | TRIPPING-KED-22-00599 | 0245/20221008/008 | Kedah | Kuala Nerang | 11kV | Underground | 08-10-2022 19:19 | PPU NAKA 4K5 | PPU NAKA 4K5 |  | Core Opened | Partly Environment | Cable | TRANSIENT | 08-10-2022 19:21 | 08-10-2022 20:02 | 41 |  |  |  | 08-10-2022 21:16 | 1.95
Northern | K1 | TRIPPING-KED-22-00601 | 0245/20221010/001 | Kedah | Kuala Nerang | 11kV | Underground | 10-10-2022 05:46 | PPU KUALA NERANG 6K5 | PDB SMK KUALA NERANG KKN00054 | TMN SRI TAMPOI KKN00669 - LADANG BATU HITAM KKN00738 | Core Opened | Partly Environment | Cable | CABLE | 10-10-2022 05:48 | 10-10-2022 06:30 | 42 | 10-10-2022 15:25 | 11-10-2022 15:59 | 24 | 11-10-2022 17:05 | 35.32
Northern | K1 | TRIPPING-PLS-22-00090 | RE/2610/20221012/PLS/00090 | Perlis | Perlis | 11kV | Underground | 12-10-2022 00:57 | PMU CHUPING CB7 | SK GUAR NANGKA KAN02604 |  |  |  |  | CABLE | 12-10-2022 01:10 | 12-10-2022 01:35 | 25 | 12-10-2022 01:45 | 13-10-2022 17:20 | 39 | 13-10-2022 17:36 | 40.65
Northern | K1 | TRIPPING-KED-22-00606 | 0242/20221012/003 | Kedah | Jitra | 11kV | Underground | 12-10-2022 06:40 | PPU CHANGLOON CL3 | PPU CHANGLOON CL3 | PAT RUMAH PAM JALAN KODIANG KJT01608 - PATOD KG. TOK BARUH KJT00988 | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 12-10-2022 07:08 | 12-10-2022 07:43 | 35 | 12-10-2022 16:36 | 13-10-2022 23:19 | 30 | 14-10-2022 00:17 | 41.62
Northern | K1 | TRIPPING-KED-22-00616 | 0245/20221015/002 | Kedah | Kuala Nerang | 11kV | Overhead | 15-10-2022 12:52 | PPU NAKA 5K5 | PDB KEDA KG. BUKIT KAS03567 CB1 | PBT KG. TELAGA ERAH KKN00760 - PAT PONG MANIS UTARA KKN00752 | Core Broken | Partly Environment | Cable | CABLE | 15-10-2022 15:40 | 15-10-2022 15:46 | 6 | 15-10-2022 18:14 | 20-10-2022 00:21 | 102 | 20-10-2022 01:07 | 108.25
Northern | K1 | TRIPPING-PLS-22-00091 | 2610/20221017/045 | Perlis | Perlis | 11kV | Underground | 17-10-2022 23:37 | PMU KANGAR CB7 | TMN BUNGA PADI KAN00388 CB1 | PDB LOJI KUMBAHAN WANG BINTONG KAN02566 - PE TMN WAN ARPAH KAN02764 | Failed, Shorted by Water Ingress | Partly Environment | Transition Joint | CABLE | 17-10-2022 23:40 | 17-10-2022 23:56 | 16 | 19-10-2022 23:26 | 22-10-2022 16:42 | 65 | 22-10-2022 17:04 | 113.45
Northern | K1 | TRIPPING-PLS-22-00092 | 2610/20221019/035 | Perlis | Perlis | 11kV | Underground | 19-10-2022 18:18 | PMU KUALA PERLIS CB7 | PDB PANGSAPURI KG.WAI KAN00647 CB1 | PLB TMN SERI BAYU KAN00630 - TMN SENTOSA KUALA PERLIS KAN00629 | Core Opened | Partly Environment | Cable | CABLE | 19-10-2022 18:20 | 19-10-2022 19:00 | 40 | 24-10-2022 10:07 | 24-10-2022 20:10 | 10 | 24-10-2022 20:24 | 122.1
Northern | K1 | TRIPPING-PLS-22-00093 | 2610/20221020/001 | Perlis | Perlis | 11kV | Underground | 20-10-2022 05:07 | PMU KANGAR CB6 | PMU KANGAR CB6 | PDB SM PADANG BOHOR - TMN SRI HARTAMAS KAN02902 | Open Circuit | Soil Movement | Straight Through Joint | CABLE | 20-10-2022 05:20 | 20-10-2022 05:32 | 12 | 23-10-2022 09:57 | 23-10-2022 22:24 | 12 | 23-10-2022 22:44 | 89.62
Northern | K1 | TRIPPING-KED-22-00639 | 0242/20221024/010 | Kedah | Jitra | 11kV | Underground | 24-10-2022 14:30 | PPU DARULAMAN 6K5 | PPU DARULAMAN 6K5 | SEKOLAH MEN SERI MAHAWANGSA - PPU DARULAMAN 6K5 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 24-10-2022 14:43 | 24-10-2022 14:55 | 12 | 24-10-2022 15:55, 24-10-2022 23:41 | 24-10-2022 16:04, 26-10-2022 13:41 | 0, 37 | 27-10-2022 16:21 | 73.85
Northern | K1 | TRIPPING-PLS-22-00094 | 2610/20221025/021 | Perlis | Perlis | 11kV | Underground | 25-10-2022 15:02 | PPU SIMPANG EMPAT CB1 | PDB KLG PADI MAJU KAN01041 CB1 | PAT PADANG PETANI - PDB KLG BERAS KUDUNG KAN01051 | Core Opened | Defective Manufacture | Cable | CABLE | 25-10-2022 15:06 | 25-10-2022 15:38 | 32 | 25-10-2022 21:03 | 14-11-2022 23:47 | 482 | 15-11-2022 00:06 | 489.07
Northern | K1 | TRIPPING-KED-22-00645 | 0245/20221026/001 | Kedah | Kuala Nerang | 11kV | Overhead | 26-10-2022 01:00 | PPU NAKA 1K5 | PPU NAKA 1K5 | PLB REBAN AYAM PONG KKN03050 - PDB INDUSTRI KEDA NAKA KKN00614 | Core Opened | Partly Environment | Cable | CABLE | 26-10-2022 01:01 | 26-10-2022 01:40 | 39 | 26-10-2022 16:12 | 28-10-2022 02:09 | 33 | 28-10-2022 02:37 | 49.62
Northern | K1 | TRIPPING-KED-22-00647 | 0242/20221026/035 | Kedah | Jitra | 11kV | Underground | 26-10-2022 11:25 | PPU KODIANG KD1 | SSBT RUMAH PAM PERING KJT01634 CB1 | PATOD R/PAM PS 1 KJT01166 - | Core Opened | Partly Environment | Cable | TRANSIENT | 26-10-2022 11:45 | 26-10-2022 12:20 | 35 |  |  |  | 26-10-2022 13:37 | 2.2
Northern | K1 | TRIPPING-KED-22-00653 | 0242/20221027/015 | Kedah | Jitra | 11kV | Underground | 27-10-2022 13:04 | PPU UUM SINTOK ST3 | PPU UUM SINTOK ST3 | PPU UUM SINTOK ST3 - SS PUSAT PEMBANGUNAN EKS UUM KJT01719 | Core Opened | Defective Manufacture | Cable | CABLE | 27-10-2022 13:06 |  | 0 | 27-10-2022 14:20, 27-10-2022 21:19 | 27-10-2022 15:15, 02-11-2022 18:34 | 0, 141 | 02-11-2022 19:48 | 150.73
Northern | K1 | TRIPPING-PLS-22-00095 | 2610/20221028/005 | Perlis | Perlis | 11kV | Overhead | 28-10-2022 08:59 | PMU KUALA PERLIS CB7 | PMU KUALA PERLIS CB7 | PMU KUALA PERLIS CB7 - PDB PERLIS MARINE KAN00650 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 28-10-2022 09:02 | 28-10-2022 09:29 | 27 | 02-11-2022 10:43 | 02-11-2022 23:23 | 12 | 03-11-2022 00:04 | 135.08
Northern | K1 | TRIPPING-KED-22-00657 | 0240/20221029/027 | Kedah | Jitra | 11kV | Underground | 29-10-2022 13:21 | PPU JERLUN SJ7 | SS 11KV SAMAK KJT19323 CB1 | PBT KUALA JERLUN 2 KJT01635 - PBT KUALA TUNJANG KJT01432 | Core Opened | Partly Environment | Cable | CABLE | 29-10-2022 13:22 | 29-10-2022 14:04 | 42 | 30-10-2022 21:49 | 31-10-2022 13:20 | 15 | 31-10-2022 14:05 | 48.73
Northern | K1 | TRIPPING-KED-22-00658 | 0240/20221029/028 | Kedah | Jitra | 11kV | Underground | 29-10-2022 13:33 | PPU JERLUN SJ1 | SM SANGLANG KJT01475 CB1 | PDB KUATERS GURU SM SANGLANG KJT19405 - PDB KLG BERAS EVERGREEN KJT01575 | Core Opened | Partly Environment | Cable | CABLE | 29-10-2022 13:35 | 29-10-2022 14:20 | 45 | 29-10-2022 20:25 | 03-11-2022 18:07 | 117 | 03-11-2022 18:59 | 125.43
Northern | K1 | TRIPPING-KED-22-00669 | 0245/20221103/013 | Kedah | Kuala Nerang | 11kV | Underground | 03-11-2022 19:34 | PPU NAKA 4K5 | PPU NAKA 4K5 | PAT KUBANG JULOK KKN00368 - PDB QTRS GURU NAKA KKN00821 | Core Opened | Partly Weather | Cable | CABLE | 03-11-2022 19:40 | 03-11-2022 20:05 | 25 | 05-11-2022 16:37 | 05-11-2022 21:34 | 4 | 05-11-2022 22:37 | 51.05
Northern | K1 | TRIPPING-PLS-22-00096 | 2610/20221104/001 | Perlis | Perlis | 11kV | Underground | 04-11-2022 01:43 | PMU KUALA PERLIS CB3 | PMU KUALA PERLIS CB3 | PBT SG. BEREMBANG KAN01206 - PDB WATER TREATMENT KAN01205 | Core Opened | Partly Environment | Cable | CABLE | 04-11-2022 01:58 |  | 0 | 04-11-2022 21:27 | 16-11-2022 21:20 | 287 | 16-11-2022 21:37 | 307.9
Northern | K1 | TRIPPING-KED-22-00675 | 0242/20221105/002 | Kedah | Jitra | 11kV | Substation | 05-11-2022 09:17 | PPU KODIANG KD1 | SSBT RUMAH PAM PERING KJT01633 CB1 |  | Tank - Internal Fault | Partly Environment | RMU SF6 | TRANSIENT | 05-11-2022 09:18 | 05-11-2022 10:02 | 44 |  |  |  | 05-11-2022 10:00 | 0.72
Northern | K1 | TRIPPING-PLS-22-00097 | 2610/20221106/008 | Perlis | Perlis | 11kV | Underground | 06-11-2022 09:49 | PMU KUALA PERLIS CB1 | PDB PROMENADE KAN01200 | TMN BUKIT KUBU FASA 2 KAN02739 - | Core Opened | Defective Manufacture | Cable | TRANSIENT | 06-11-2022 10:23 | 06-11-2022 11:00 | 37 |  |  |  | 06-11-2022 12:15 | 2.43
Northern | K1 | TRIPPING-PLS-22-00098 | RE/2610/20221106/PLS/00098 | Perlis | Perlis | 11kV | Underground | 06-11-2022 11:06 | PPU BUKIT KETERI 5K5 | PDB TMN SRI PUTERI KAN02605 | RE(RSO) OUTREACH GREEN 1 B1 - |  |  |  | CABLE | 06-11-2022 11:30 | 06-11-2022 12:05 | 35 | 06-11-2022 13:11 | 06-11-2022 23:39 | 10 | 06-11-2022 23:55 | 12.82
Northern | K1 | TRIPPING-KED-22-00687 | 0242/20221110/015 | Kedah | Jitra | 11kV | Underground | 10-11-2022 12:06 | PPU DARULAMAN 12K5 | PPU DARULAMAN 12K5 | PPU DARULAMAN 12K5 - PDB ONKYO KJT01717 | Core Opened | Defective Manufacture | Cable | CABLE, CABLE | 10-11-2022 12:08 | 10-11-2022 12:27 | 19 | 10-11-2022 21:10 | 13-11-2022 22:08 | 72 | 13-11-2022 23:15 | 83.15
Northern | K1 | TRIPPING-PLS-22-00099 | RE/2610/20221110/PLS/00099 | Perlis | Perlis | 11kV | Underground | 10-11-2022 17:33 | PPU PADANG BESAR CB16 | PPU PADANG BESAR CB16 | PPU PADANG BESAR CB16 - |  |  |  | NO FAULT | 10-11-2022 17:33 | 10-11-2022 18:00 | 27 | 10-11-2022 18:58 | 11-11-2022 00:29 | 5 | 11-11-2022 01:00 | 7.45
Northern | K1 | TRIPPING-KED-22-00690 | 0242/20221110/055 | Kedah | Jitra | 11kV | Overhead | 10-11-2022 22:51 | PPU KODIANG KD5 | PPU KODIANG KD5 | PDB RUMAH PAM SG. PERING KJT01276 - PLB TALIKOM PDG SERA KJT01277 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 10-11-2022 22:53 | 10-11-2022 23:30 | 37 | 11-11-2022 22:24 | 12-11-2022 18:17 | 19 | 12-11-2022 19:32 | 44.68
Northern | K1 | TRIPPING-KED-22-00691 | 0242/20221111/016 | Kedah | Jitra | 11kV | Underground | 11-11-2022 12:21 | PPU LOJI AIR ARAU GIS 12K5 | PPU LOJI AIR ARAU GIS 12K5 | PPU LOJI AIR ARAU GIS 12K5 - R/PAM SG PERING KJT19144, - R/PAM SG PERING KJT19143 - PLB LPN LANA BULU KJT19104 | Core Opened | Defective Manufacture | Cable | CABLE, CABLE | 11-11-2022 12:22 | 11-11-2022 13:05 | 43 | 11-11-2022 19:28, 11-11-2022 19:29 | 12-11-2022 18:15, 12-11-2022 18:16 | 22, 22 | 12-11-2022 20:40 | 32.32
Northern | K1 | TRIPPING-KED-22-00696 | 0242/20221113/014 | Kedah | Jitra | 11kV | Underground | 13-11-2022 12:10 | PMU TANJUNG PAUH TP18 | KLG RUBBER SEALS KJT18919 CB1 | PDB ONKYO KJT00535 - KLG RUBBER SEALS KJT18919 | Core Opened | Defective Manufacture | Cable | CABLE | 13-11-2022 12:50 | 13-11-2022 13:02 | 12 | 13-11-2022 15:34 | 13-11-2022 22:11 | 6 | 13-11-2022 23:30 | 11.33
Northern | K1 | TRIPPING-PLS-22-00100 | 2610/20221114/005 | Perlis | Perlis | 11kV | Underground | 14-11-2022 01:51 | PMU KUALA PERLIS CB1 | PMU KUALA PERLIS CB1 | PDB KLG AIR BATU (LKIM) KAN00156 - TMN SENTOSA KUALA PERLIS KAN00627 | Core Opened | Partly Environment | Cable | CABLE | 14-11-2022 02:05 | 14-11-2022 02:20 | 15 | 16-11-2022 00:26, 23-11-2022 12:02 | 22-11-2022 13:32, 23-11-2022 19:32 | 157, 7 | 23-11-2022 19:42 | 233.85
Northern | K1 | TRIPPING-PLS-22-00101 | 2610/20221114/025 | Perlis | Perlis | 11kV | Underground | 14-11-2022 10:01 | PMU CHUPING CB8 | PMU CHUPING CB8 | TAE HWA - PMU CHUPING CB8 | Open Circuit | Soil Movement | Straight Through Joint | CABLE | 14-11-2022 10:06 | 14-11-2022 10:45 | 39 | 15-11-2022 22:01 | 17-11-2022 23:24 | 49 | 17-11-2022 23:33 | 85.53
Northern | K1 | TRIPPING-KED-22-00702 | 0242/20221115/004 | Kedah | Jitra | 11kV | Underground | 15-11-2022 08:54 | PMU TANJUNG PAUH TP15 | PDB IBUSAWAT TELEKOM JTR-TLKOM KJT00460 CB1 | PDB TMN PASU - PDB MADA JITRA | Core Opened | Partly Environment | Cable | CABLE | 15-11-2022 09:00 | 15-11-2022 09:25 | 25 | 15-11-2022 21:33 | 17-11-2022 18:10 | 44 | 17-11-2022 19:47 | 58.88
Northern | K1 | TRIPPING-KED-22-00707 | 0242/20221117/002 | Kedah | Jitra | 11kV | Underground | 17-11-2022 01:43 | PMU BUKIT KAYU HITAM BKH4 | PMU BUKIT KAYU HITAM BKH4 | S/S RMU BATU 26 KJT00823 - SSD NO.1 KJT00824 | Core Opened | Partly Environment | Cable | CABLE | 17-11-2022 01:50 | 17-11-2022 02:20 | 30 | 17-11-2022 23:48 | 21-11-2022 20:19 | 92 | 21-11-2022 20:19 | 114.6
Northern | K1 | TRIPPING-KED-22-00711 | 0245/20221118/002 | Kedah | Kuala Nerang | 11kV | Underground | 18-11-2022 02:48 | PPU KUALA NERANG CB4 | PDB SMK KUALA NERANG KKN00054 CB1 | PLB BUKIT TEMBAGA SELATAN KKN00100 - PLB BKT TEMBAGA KKN00102 | Core Opened | Partly Environment | Cable | CABLE | 18-11-2022 02:50 | 18-11-2022 03:18 | 28 | 18-11-2022 15:51, 22-11-2022 23:18 | 22-11-2022 21:07, 23-11-2022 16:09 | 101, 16 | 23-11-2022 16:30 | 133.7
Northern | K1 | TRIPPING-PLS-22-00102 | 2610/20221120/027 | Perlis | Perlis | 11kV | Underground | 20-11-2022 11:58 | PMU KANGAR CB12 | PVCB TMN MERPATI KAN03103 CB1 | PDB PERINDUSTRIAN RINGAN KAN00726 - ADVANCE CHICKEN KAN02352 | Core Opened | Partly Environment | Cable | CABLE | 20-11-2022 12:00 | 20-11-2022 12:40 | 40 | 20-11-2022 21:49, 30-11-2022 00:27 | 29-11-2022 11:22, 30-11-2022 00:09, 09-12-2022 08:16 | 218, 223 | 09-12-2022 08:25 | 452.45
Northern | K1 | TRIPPING-KED-22-00721 | 0242/20221123/006 | Kedah | Jitra | 11kV | Overhead | 23-11-2022 10:28 | PPU LOJI AIR ARAU GIS 11K5 | PDB KLG BERAS PERING KJT01775 CB1 |  | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | TRANSIENT | 23-11-2022 10:30 | 23-11-2022 11:30 | 60 |  |  |  | 23-11-2022 12:50 | 2.37
Northern | K1 | TRIPPING-PLS-22-00103 | 2610/20221128/031 | Perlis | Perlis | 11kV | Underground | 28-11-2022 16:55 | PMU KUALA PERLIS CB8 | PMU KUALA PERLIS CB8 | PDB INDUSTRI MARA (KIM) - PDB INDUSTRI MARA (KIM) KAN02780 | Core Opened | Partly Environment | Cable | CABLE | 28-11-2022 17:00 | 28-11-2022 17:25 | 25 | 30-11-2022 14:09 | 06-12-2022 23:46 | 153 | 06-12-2022 23:56 | 199.02
Northern | K1 | TRIPPING-KED-22-00730 | 0242/20221129/016 | Kedah | Jitra | 11kV | Underground | 29-11-2022 15:19 | PPU DARULAMAN 11K5 | PPU DARULAMAN 11K5 | PDB KLG DANCAST - PPU DARULAMAN 11K5 | Core Opened | Partly Environment | Cable | CABLE | 29-11-2022 15:26 | 29-11-2022 15:38 | 12 | 30-11-2022 21:17 | 01-12-2022 18:01 | 20 | 01-12-2022 19:00 | 51.68
Northern | K1 | TRIPPING-PLS-22-00104 | 2610/20221203/011 | Perlis | Perlis | 11kV | Underground | 03-12-2022 15:51 | PPU LOJI AIR ARAU GIS 4K5 | PPU LOJI AIR ARAU GIS 4K5 | PLB PADANG TELELA KAN00926 - PDB RPA PEKAN PAUH KAN00874 | Core Opened | Partly Environment | Cable | CABLE | 03-12-2022 15:57 | 03-12-2022 16:20 | 23 |  |  |  | 10-12-2022 12:58 | 165.12
Northern | K1 | TRIPPING-PLS-22-00105 | 2610/20221204/017 | Perlis | Perlis | 11kV | Underground | 04-12-2022 21:54 | PPU LOJI AIR ARAU GIS 5K5 | PPU LOJI AIR ARAU GIS 5K5 | PDB BERNAS ARAU - PDB ISTANA ARAU-VVIP | Core Opened | Partly Environment | Cable | CABLE | 04-12-2022 21:56 | 04-12-2022 22:40 | 44 | 05-12-2022 21:09 | 13-12-2022 11:19 | 182 | 13-12-2022 11:22 | 205.47
Northern | K1 | TRIPPING-PLS-22-00106 | 2610/20221205/004 | Perlis | Perlis | 11kV | Underground | 05-12-2022 05:47 | PPU SHORUBBER CB5 | BEHOR MENTALOON KAN00974 CB1 |  | Core Opened | Partly Environment | Cable | TRANSIENT | 05-12-2022 05:49 | 05-12-2022 06:30 | 41 |  |  |  | 05-12-2022 06:55 | 1.13
Northern | K1 | TRIPPING-PLS-22-00107 | 2610/20221205/023 | Perlis | Perlis | 11kV | Substation | 05-12-2022 15:24 | PMU KUALA PERLIS CB1 | PMU KUALA PERLIS CB1 | TMN BUKIT KUBU FASA 2 KAN02740 - PDB PROCESSING FACTORY KAN00626 | Damaged by Third Party | Partly Environment | H-Pole | CABLE | 05-12-2022 15:24 | 05-12-2022 16:05 | 41 | 07-12-2022 10:28 | 07-12-2022 23:20 | 12 | 07-12-2022 23:38 | 56.23
Northern | K1 | TRIPPING-KED-22-00753 | 0242/20221208/017 | Kedah | Jitra | 11kV | Underground | 08-12-2022 15:51 | PMU TANJUNG PAUH TP9 | PMU TANJUNG PAUH TP9 | PMU TANJUNG PAUH TP9 - PDB KLJ HEIGHT NO.7 KJT00545 | Core Opened | Defective Manufacture | Cable | CABLE | 08-12-2022 15:55 | 08-12-2022 16:25 | 30 | 08-12-2022 21:21 | 12-12-2022 20:32 | 95 | 12-12-2022 21:20 | 101.48
Northern | K1 | TRIPPING-KED-22-00755 | 0245/20221210/001 | Kedah | Kuala Nerang | 11kV | Overhead | 10-12-2022 10:07 | PPU NAKA 5K5 | PPU NAKA 5K5 | PBT PAYA SIDANG - PPU NAKA 5K5 | Snapped | Partly Environment | ABC Conductor | CABLE | 10-12-2022 10:09 | 10-12-2022 11:10 | 61 | 10-12-2022 17:55 | 11-12-2022 23:33 | 29 | 11-12-2022 23:50 | 37.72
Northern | K1 | TRIPPING-PLS-22-00109 | 2610/20221212/022 | Perlis | Perlis | 11kV | Underground | 12-12-2022 16:23 | PPU PADANG BESAR CB9 | PDB TITI TINGGI KAN00091 CB1 | PBT BUKIT CABANG KAN02101 - PLB SMPG JALAN SAHABAT KAN02266 | Insulation Burnt | Partly Environment | Cable Termination | OVERHEAD LINES | 12-12-2022 16:31 | 12-12-2022 17:10 | 39 | 13-12-2022 13:04 | 15-12-2022 22:28 | 57 | 15-12-2022 22:44 | 78.35
Northern | K1 | TRIPPING-PLS-22-00110 | 2610/20221213/004 | Perlis | Perlis | 11kV | Underground | 13-12-2022 07:53 | PPU SIMPANG EMPAT CB5 | SEK MEN SANGLANG KAN01095 CB1 | PDB K/UDANG RAMADIN KAN01130 - PDB KOLAM UDANG YAYASAN ISLAM KAN01131 | Core Opened | Partly Environment | Cable | CABLE | 13-12-2022 07:56 | 13-12-2022 08:25 | 29 | 13-12-2022 22:35, 25-12-2022 09:20 | 25-12-2022 08:41, 25-12-2022 23:13 | 274, 13 | 25-12-2022 23:45 | 303.87
Northern | K1 | TRIPPING-PLS-22-00111 | 2610/20221216/002 | Perlis | Perlis | 11kV | Underground | 16-12-2022 01:28 | PPU LOJI AIR ARAU GIS 8K5 | PVCB RUMAH PAM GUAR SANJI KAN00958 | PAT KG. BAKONG-KAN KAN00963 - BELAT BATU KAN00960 | Core Opened | Defective Manufacture | Cable | CABLE | 16-12-2022 01:30 | 16-12-2022 02:10 | 40 | 16-12-2022 17:22 | 20-12-2022 21:43 | 100 | 20-12-2022 22:05 | 116.62
Northern | K1 | TRIPPING-KED-22-00765 | 0242/20221222/002 | Kedah | Jitra | 11kV | Underground | 22-12-2022 07:58 | PPU KODIANG KD2 | PDB SM TUNKU BENDAHARA KJT01260 CB1 | PLB KG. PERING KJT01173 - PBT KG. WANG KJT01172 | Core Opened | Partly Environment | Cable | CABLE | 22-12-2022 08:15 | 22-12-2022 08:41 | 26 | 26-12-2022 09:05 | 26-12-2022 20:06 | 11 | 26-12-2022 20:17 | 108.32
Northern | K1 | TRIPPING-KED-22-00766 | 0242/20221222/011 | Kedah | Jitra | 11kV | Underground | 22-12-2022 10:41 | PMU BUKIT KAYU HITAM BKH5 | BAYAN MAS NO.2 KJT01825 CB1 | PDB KOMP LAKA TEMIN KJT01100 - PDB BALAI POLIS LAKA TEMIN-NOP KJT01101 | Core Opened | Partly Environment | Cable | CABLE | 22-12-2022 10:54 | 22-12-2022 11:27 | 33 | 22-12-2022 21:57 | 26-12-2022 19:04 | 93 | 26-12-2022 19:33 | 104.87
Northern | K1 | TRIPPING-PLS-22-00112 | 2610/20221223/002 | Perlis | Perlis | 11kV | Underground | 23-12-2022 00:20 | PPU MINI PPU ABI 1K5 | PPU MINI PPU ABI 1K5 | PLB KUARI BATU TEONG CHAI KAN00317 - PDB SMPG ABI KAN00316 |  |  |  | CABLE | 23-12-2022 01:51 | 23-12-2022 02:25 | 34 | 23-12-2022 20:19 | 02-01-2023 23:48 | 243 | 03-01-2023 00:06 | 263.77
Northern | K1 | TRIPPING-KED-22-00769 | 0245/20221225/003 | Kedah | Kuala Nerang | 11kV | Underground | 25-12-2022 09:04 | PPU KUALA NERANG 4K5 | PPU KUALA NERANG 4K5 | PDB TELEKOM KUALA NERANG KKN00002 - PDB KOMP PEKAN SELASA KKN00004 | Insulation Breakdown | Insulation Deterioration | Cable Termination | CABLE | 25-12-2022 09:06 |  | 0 | 27-12-2022 14:39 | 27-12-2022 20:05 | 5 | 27-12-2022 20:23 | 59.32
Northern | K1 | TRIPPING-PLS-23-00001 | 2610/20230101/002 | Perlis | Perlis | 11kV | Overhead | 01-01-2023 08:57 | PPU PADANG BESAR CB9 | PPU PADANG BESAR CB9 | PDB TITI TINGGI - PPU PADANG BESAR CB9 | Insulation Failed, Shorted by Old External Damage | Partly Environment | Cable Termination | OVERHEAD LINES | 01-01-2023 09:00 | 01-01-2023 09:45 | 45 | 01-01-2023 17:22 | 01-01-2023 18:37 | 1 | 02-01-2023 19:56 | 34.98
Northern | K1 | TRIPPING-PLS-23-00002 | 2610/20230106/015 | Perlis | Perlis | 11kV | Underground | 06-01-2023 19:43 | PPU SHORUBBER CB5 | BEHOR MENTALOON KAN00974 CB1 |  | Core Opened | Partly Environment | Cable | TRANSIENT | 06-01-2023 19:44 | 06-01-2023 20:06 | 22 |  |  |  | 06-01-2023 20:48 | 1.08
Northern | K1 | TRIPPING-PLS-23-00003 | 2610/20230111/002 | Perlis | Perlis | 11kV | Underground | 11-01-2023 01:30 | PPU SIMPANG EMPAT CB6 | PPU SIMPANG EMPAT CB6 | PPU SIMPANG EMPAT CB6 - PLB BANK PERTANIAN KAN01150 | Core Opened | Partly Environment | Cable | CABLE | 11-01-2023 01:38 | 11-01-2023 02:16 | 38 | 11-01-2023 15:48 | 11-01-2023 22:11 | 6 | 12-01-2023 21:26 | 43.93
Northern | K1 | TRIPPING-KED-23-00026 | 0242/20230115/001 | Kedah | Jitra | 11kV | Underground | 15-01-2023 03:39 | PMU BUKIT KAYU HITAM BKH5 | BAYAN MAS NO.2 KJT01825 CB1 | PDB R/AWAM LAKA TEMIN KJT01086 - PDB LDG RAKYAT KJT01087 | Core Opened | Partly Environment | Cable | CABLE | 15-01-2023 03:44 | 15-01-2023 04:25 | 41 | 15-01-2023 21:31 | 18-01-2023 21:52 | 72 | 18-01-2023 22:10 | 90.52
Northern | K1 | TRIPPING-KED-23-00030 | 0242/20230115/030 | Kedah | Jitra | 11kV | Overhead | 15-01-2023 14:32 | PMU TANJUNG PAUH TP20 | TMN PELANGI JITRA KJT01863 CB1 | TMN PELANGI JITRA KJT01863 - PBT STN PAM MADA PULAU KETAM KJT01829 | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 15-01-2023 14:32 | 15-01-2023 14:38 | 6 | 15-01-2023 23:32 | 17-01-2023 20:58 | 45 | 17-01-2023 21:50 | 55.3
Northern | K1 | TRIPPING-KED-23-00035 | 0242/20230115/075 | Kedah | Jitra | 11kV | Underground | 15-01-2023 23:26 | PPU JERLUN SJ6 | PPU JERLUN SJ6 | PBT LUBOK AIR KJT01488 - PBT PERMATANG PAKU KJT01489 | Core Opened | Partly Environment | Cable | CABLE | 15-01-2023 23:28 | 15-01-2023 23:55 | 27 | 16-01-2023 20:45 | 05-02-2023 20:37 | 479 | 05-02-2023 21:11 | 501.75
Northern | K1 | TRIPPING-KED-23-00044 | 0245/20230118/016 | Kedah | Kuala Nerang | 11kV | Underground | 18-01-2023 16:16 | PPU KUALA NERANG 3K5 | PPU KUALA NERANG 3K5 | PBT KG. MALAU-ALS KKN00238 - PLB KG. TENGAH-KNRG KKN00240 | Core Opened | Partly Environment | Cable | CABLE | 18-01-2023 16:31 | 18-01-2023 16:55 | 24 | 18-01-2023 20:49 | 19-01-2023 20:01 | 23 | 19-01-2023 20:48 | 28.53
Northern | K1 | TRIPPING-KED-23-00048 | 0245/20230119/006 | Kedah | Kuala Nerang | 11kV | Underground | 19-01-2023 12:21 | PPU KUALA NERANG 5K5 | PDB TMN AKASIA KKN00582 CB1 | LGM SG SARI KKN00787 - PPU MINI PPU L/AIR PDG SANAI LA2 | Core Opened | Partly Environment | Cable | CABLE | 19-01-2023 14:41 | 19-01-2023 15:05 | 24 | 21-01-2023 11:24 | 21-01-2023 19:17 | 7 | 21-01-2023 20:00 | 55.65
Northern | K1 | TRIPPING-KED-23-00060 | 0242/20230126/019 | Kedah | Jitra | 11kV | Underground | 26-01-2023 20:16 | PPU DARULAMAN 10K5 | PPU DARULAMAN 10K5 | MUTIARA RESIDENT NO 2 KJT19312 - MUTIARA RESIDENT NO 1 KJT19311 | Core Opened | Partly Environment | Cable | CABLE | 26-01-2023 20:25 | 26-01-2023 20:50 | 25 | 26-01-2023 23:42 | 31-01-2023 23:42 | 120 | 01-02-2023 00:48 | 124.53
Northern | K1 | TRIPPING-KED-23-00061 | 0245/20230128/007 | Kedah | Kuala Nerang | 11kV | Underground | 28-01-2023 21:16 | PPU NAKA 4K5 | PDB BDR BARU NAKA KKN00375 | PBT KG. DATOK KKN00392 - PBT KG. SIREH KKN00394 | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 28-01-2023 21:44 | 28-01-2023 22:01 | 17 | 29-01-2023 09:54 | 30-01-2023 22:19 | 36 | 30-01-2023 22:28 | 49.2
Northern | K1 | TRIPPING-KED-23-00067 | 0245/20230130/007 | Kedah | Kuala Nerang | 11kV | Underground | 30-01-2023 16:22 | PPU MINI PPU L/AIR PDG SANAI LA3 | PPU MINI PPU L/AIR PDG SANAI LA3 | PBT KG. BARU PADANG SANAI KKN00700 - SMPG EMPAT EMPANGAN AHNING KKN00654 | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 30-01-2023 16:44 | 30-01-2023 17:25 | 41 | 31-01-2023 10:30, 18-02-2023 10:08 | 01-02-2023 12:14, 20-02-2023 20:41 | 25, 58 | 21-02-2023 12:57 | 524.58
Northern | K1 | TRIPPING-KED-23-00069 | 0245/20230201/003 | Kedah | Kuala Nerang | 11kV | Overhead | 01-02-2023 10:42 | PPU NAKA 1K5 | PPU NAKA 1K5 | PLB RMU PPU NAKA KKN00573 - PDB IKBN PEDU 1 KKN00552 | Insulation Failed, Shorted by Water Ingress | Partly Environment | Cable Termination | CABLE | 01-02-2023 10:43 | 01-02-2023 11:05 | 22 | 01-02-2023 21:42 | 03-02-2023 00:21 | 26 | 03-02-2023 00:38 | 37.93
Northern | K1 | TRIPPING-KED-23-00073 | 0242/20230203/006 | Kedah | Jitra | 11kV | Overhead | 03-02-2023 13:09 | PPU DARULAMAN 10K5 | PPU DARULAMAN 10K5 | MUTIARA RESIDENT NO 2 KJT19315 - STN SUIS 11KV IKBN JITRA KJT18895 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 03-02-2023 13:12 | 03-02-2023 13:40 | 28 | 03-02-2023 20:16 | 06-02-2023 18:13 | 69 | 06-02-2023 18:50 | 77.68
Northern | K1 | TRIPPING-PLS-23-00004 | 2610/20230205/022 | Perlis | Perlis | 11kV | Underground | 05-02-2023 11:48 | PPU POLITEKNIK PAUH PERLIS 2 | PPU POLITEKNIK PAUH PERLIS CB2 | MRSM ULU PAUH KAN02113 - TMN KURUNG ANAI KAN02837 | Core Opened | Partly Environment | Cable | CABLE | 05-02-2023 12:46 | 05-02-2023 13:20 | 34 | 07-02-2023 21:43 | 11-02-2023 23:21 | 97 | 11-02-2023 23:55 | 156.12
Northern | K1 | TRIPPING-KED-23-00080 | 0240/20230210/001 | Kedah | Jitra | 11kV | Underground | 10-02-2023 00:42 | PMU TANJUNG PAUH IB36 | PMU TANJUNG PAUH CB36 | PAUH 132/11KV T4 - |  |  |  | NO FAULT | 10-02-2023 01:25 |  | 0 | 10-02-2023 02:28 | 11-02-2023 14:53 | 36 | 11-02-2023 16:24 | 39.7
Northern | K1 | TRIPPING-PLS-23-00005 | 2610/20230210/008 | Perlis | Perlis | 11kV | Underground | 10-02-2023 11:40 | PMU KUALA PERLIS CB2 | PERLIS SPECIALIST HOSPITAL KAN02779 CB1 | TMN BUNGA PADI KAN00386 - TMN BINTONG CERIA KAN02791 | Core Opened | Partly Environment | Cable | CABLE | 10-02-2023 11:49 | 10-02-2023 11:59 | 10 | 10-02-2023 21:32 | 14-02-2023 23:20 | 97 | 14-02-2023 23:35 | 107.92
Northern | K1 | TRIPPING-PLS-23-00007 | 0260/20230211/001 | Perlis | Perlis | 11kV | Underground | 11-02-2023 04:57 | PPU SIMPANG EMPAT CB7 | PPU SIMPANG EMPAT CB7 | TMN PELANGI-KAN - PPU SIMPANG EMPAT CB7 | Core Opened | Defective Manufacture | Cable | CABLE | 11-02-2023 05:03 | 11-02-2023 05:47 | 44 | 12-02-2023 21:37, 03-03-2023 18:20 | 03-03-2023 16:57, 04-03-2023 08:54 | 451, 14 | 04-03-2023 09:08 | 508.18
Northern | K1 | TRIPPING-PLS-23-00008 | 2610/20230219/001 | Perlis | Perlis | 11kV | Underground | 19-02-2023 05:25 | PMU CHUPING CB10 | PDB UITM ARAU KAN00865 CB1 | PAT ALOR ARA TIMUR KAN01867 - PDB SK KUBANG GAJAH KAN00829 | Core Opened | Partly Environment | Cable | CABLE | 19-02-2023 05:27 | 19-02-2023 06:00 | 33 | 19-02-2023 21:46 | 22-02-2023 01:51 | 52 | 22-02-2023 02:09 | 68.73
Northern | K1 | TRIPPING-PLS-23-00009 | 2610/20230221/009 | Perlis | Perlis | 11kV | Underground | 21-02-2023 02:00 | PMU KUALA PERLIS CB5 | PMU KUALA PERLIS CB5 | PLB LOT 764 TMN KUALA PERLIS KAN01181 - KLG AIS IGLOO KAN02065 | Core Opened | Partly Environment | Cable | CABLE | 21-02-2023 02:02 | 21-02-2023 02:45 | 43 | 22-02-2023 19:31 | 25-02-2023 22:47 | 75 | 25-02-2023 23:27 | 117.45
Northern | K1 | TRIPPING-PLS-23-00010 | 2610/20230226/004 | Perlis | Perlis | 11kV | Substation | 26-02-2023 09:06 | PPU BUKIT KETERI 7K5 | PDB TMN BESERI JAYA KAN00176 |  | Shorted by Animal | Partly Environment | Transformer Bushing | TRANSIENT | 26-02-2023 09:07 | 26-02-2023 09:48 | 41 |  |  |  | 26-02-2023 09:49 | 0.72
Northern | K1 | TRIPPING-KED-23-00115 | 0242/20230301/030 | Kedah | Jitra | 11kV | Underground | 01-03-2023 22:18 | PPU DARULAMAN 3K5 | PPU DARULAMAN 3K5 | PDB TMN BELIMBING NO.2 JITRA KJT19075 - PATOD KG. PENIA KJT00229 | Core Opened | Partly Environment | Cable | CABLE | 01-03-2023 22:25 | 01-03-2023 22:40 | 15 | 02-03-2023 21:20 | 05-03-2023 21:01 | 71 | 05-03-2023 21:54 | 95.6
Northern | K1 | TRIPPING-KED-23-00118 | 0242/20230302/008 | Kedah | Jitra | 11kV | Overhead | 02-03-2023 08:29 | PPU DARULAMAN 6K5 | PPU DARULAMAN 6K5 | PPU DARULAMAN 6K5 - SEKOLAH MEN SERI MAHAWANGSA KJT19070 | Failed, Shorted by Corrosive Evmnt | Partly Environment | Straight Through Joint | OVERHEAD LINES | 02-03-2023 08:35 | 02-03-2023 08:50 | 15 | 03-03-2023 01:10 | 08-03-2023 19:49 | 138 | 09-03-2023 22:42 | 182.22
Northern | K1 | TRIPPING-KED-23-00123 | 0245/20230303/001 | Kedah | Kuala Nerang | 11kV | Underground | 03-03-2023 04:45 | PPU NAKA 3K5 | PPU NAKA 3K5 | PBT KUBANG KENYENG KKN00183 - KEDA KBG KENYENG 2 KKN00819 | Core Opened | Partly Environment | Cable | CABLE | 03-03-2023 05:01 | 03-03-2023 05:45 | 44 | 03-03-2023 06:50 | 05-03-2023 20:47 | 61 | 05-03-2023 21:07 | 64.37
Northern | K1 | TRIPPING-KED-23-00129 | 0245/20230306/014 | Kedah | Kuala Nerang | 11kV | Underground | 06-03-2023 16:09 | PPU KUALA NERANG 3K5 | A/R KG. TENGAH | PATOD KG.BUKIT PERIK KKN00245 - PBT KG. PERIK KKN00247 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 06-03-2023 17:21 |  | 0 | 06-03-2023 18:15 | 08-03-2023 10:47 | 40 | 09-03-2023 10:15 | 66.1
Northern | K1 | TRIPPING-KED-23-00132 | 0242/20230307/002 | Kedah | Jitra | 11kV | Underground | 07-03-2023 02:24 | PPU KEPALA BATAS KB3 | P/E TMN NURI KJT19020 | P/E TMN NURI KJT19020 - S/S KG PADANG KJT00590 | Core Opened | Defective Manufacture | Cable | CABLE | 07-03-2023 02:33 | 07-03-2023 03:09 | 36 | 07-03-2023 21:27 | 09-03-2023 21:21 | 47 | 09-03-2023 22:04 | 67.67
Northern | K1 | TRIPPING-PLS-23-00011 | 2610/20230307/046 | Perlis | Perlis | 11kV | Underground | 07-03-2023 14:40 | PMU KANGAR CB3 | PDB KOMP KASTAM KANGAR KAN00494 CB1 | PDT SK PAYA KAN02142 - POLIKLINIK BESERI-VVIP KAN00304 | Core Opened | Partly Environment | Cable | CABLE | 07-03-2023 14:55 | 07-03-2023 15:10 | 15 | 08-03-2023 22:43, 12-03-2023 11:04 | 12-03-2023 10:45, 12-03-2023 22:03 | 84, 10 | 12-03-2023 22:13 | 127.55
Northern | K1 | TRIPPING-PLS-23-00012 | 2610/20230308/070 | Perlis | Perlis | 11kV | Underground | 08-03-2023 20:09 | PPU BUKIT KETERI 7K5 | PDB TMN BESERI JAYA KAN00178 | PDB MRSM BESERI KAN00187 - PBT LMBH BIAK KAN00188 | Core Opened | Partly Environment | Cable | CABLE | 08-03-2023 20:11 | 08-03-2023 20:40 | 29 | 10-03-2023 22:26 | 28-03-2023 18:21 | 427 | 28-03-2023 18:51 | 478.7
Northern | K1 | TRIPPING-PLS-23-00013 | 2610/20230311/001 | Perlis | Perlis | 11kV | Underground | 11-03-2023 03:07 | PPU LOJI AIR ARAU GIS 3K5 | PPU LOJI AIR ARAU GIS 3K5 | PUSAT KOMERSIL ARAU NO1 KAN01981 - PUSAT KOMERSIL ARAU NO 2 KAN01986, - PUSAT KOMERSIL ARAU NO 2 KAN01985 - PDB SMK AGAMA ALAWIYAH ARAU KAN00900 | Core Opened | Partly Environment | Cable | CABLE | 11-03-2023 03:23 | 11-03-2023 04:07 | 44 | 11-03-2023 23:32 | 15-03-2023 08:39 | 81 | 15-03-2023 09:01 | 101.9
Northern | K1 | TRIPPING-PLS-23-00014 | 2610/20230312/016 | Perlis | Perlis | 11kV | Underground | 12-03-2023 12:15 | PPU SIMPANG EMPAT CB9 | PPU SIMPANG EMPAT CB9 | PPU SIMPANG EMPAT CB9 - | Core Opened | Defective Manufacture | Cable | NO FAULT | 12-03-2023 12:20 | 12-03-2023 12:43 | 23 |  |  |  | 12-03-2023 13:30 | 1.25
Northern | K1 | TRIPPING-KED-23-00143 | 0242/20230312/071 | Kedah | Jitra | 11kV | Underground | 12-03-2023 23:15 | PMU TANJUNG PAUH TP15 | PDB IBUSAWAT TELEKOM JTR-TLKOM KJT00460 CB1 | PDB MADA JITRA KJT00471 - PDB TMN PASU KJT00468 | Core Opened | Partly Environment | Cable | CABLE | 12-03-2023 23:19 | 12-03-2023 23:50 | 31 | 13-03-2023 00:06, 13-03-2023 21:14 | 13-03-2023 00:09, 26-06-2023 11:15 | 0, 2510 | 26-06-2023 11:56 | 2532.68
Northern | K1 | TRIPPING-KED-23-00151 | 0242/20230316/030 | Kedah | Jitra | 11kV | Underground | 16-03-2023 14:24 | PPU KODIANG KD1 | SSBT RUMAH PAM PERING KJT01634 | PDB KLG BAJA MK HOSBA KJT01692 - PDT YUNG HENG POULTRY KJT19442, - PADAT YUNG HENG POULTRY 2 KJT19453 - PAT CEROK MOKAM 2 KJT01220 | Failed, Shorted by Water Ingress | Poor Workmanship | Straight Through Joint | OVERHEAD LINES, CABLE | 16-03-2023 14:36 | 16-03-2023 15:04 | 28 | 16-03-2023 22:32, 16-03-2023 22:30 | 19-03-2023 20:13, 18-03-2023 20:29 | 69, 45 | 19-03-2023 21:05 | 78.68
Northern | K1 | TRIPPING-KED-23-00152 | 0242/20230316/085 | Kedah | Jitra | 11kV | Underground | 16-03-2023 16:53 | PPU CHANGLOON CL2 | PDB TMN MERBAU KJT18965 CB1 | PBT BATU 25 KJT00871 - PDT SEMARAK API NO.3 KJT19402 | Core Opened | Partly Environment | Cable | CABLE | 16-03-2023 16:55 | 16-03-2023 17:30 | 35 | 17-03-2023 01:21 | 22-03-2023 19:55 | 138 | 22-03-2023 21:05 | 148.2
Northern | K1 | TRIPPING-KED-23-00155 | 0245/20230318/002 | Kedah | Kuala Nerang | 11kV | Underground | 18-03-2023 08:04 | PPU PEDU KKN00798 | PPU PEDU KKN00798 | PBT SMPG EMPAT PEDU KKN00645 - PATOD EMPANGAN PEDU KKN00151 | Core Opened | Partly Environment | Cable | CABLE | 18-03-2023 08:08 | 18-03-2023 08:47 | 39 | 18-03-2023 09:23, 20-03-2023 22:07 | 20-03-2023 15:10, 21-03-2023 13:45 | 53, 15 | 22-03-2023 01:20 | 89.27
Northern | K1 | TRIPPING-KED-23-00163 | 0242/20230319/086 | Kedah | Jitra | 11kV | Substation | 19-03-2023 22:11 | PMU TANJUNG PAUH TP19 | PMU TANJUNG PAUH TP19 | P/P RENCAH NIAGA - | Core Opened | Partly Environment | Cable | SWITCHGEAR | 19-03-2023 22:13 | 19-03-2023 22:50 | 37 | 21-03-2023 09:01 | 21-03-2023 18:33 | 9 | 21-03-2023 19:21 | 45.17
Northern | K1 | TRIPPING-KED-23-00164 | 0242/20230319/061 | Kedah | Jitra | 11kV | Underground | 19-03-2023 22:11 | PMU TANJUNG PAUH TP20 | PMU TANJUNG PAUH TP20 | PMU TANJUNG PAUH TP20 - PLB TMN KENANGA-JITRA | Core Opened | Partly Environment | Cable | CABLE | 19-03-2023 22:13 | 19-03-2023 22:50 | 37 | 21-03-2023 01:06 | 15-05-2023 23:15 | 1342 | 17-05-2023 01:15 | 1395.07
Northern | K1 | TRIPPING-KED-23-00165 | 0242/20230319/273 | Kedah | Jitra | 11kV | Underground | 19-03-2023 23:37 | PMU TANJUNG PAUH TP14 | PMU TANJUNG PAUH TP14 | SS R/AWAM TG PAUH - PDB BANGLO NO.2-VVIP | Core Opened | Partly Environment | Cable | CABLE | 20-03-2023 00:00 | 20-03-2023 00:45 | 45 | 21-03-2023 00:17 | 24-03-2023 10:22 | 82 | 24-03-2023 11:21 | 107.73
Northern | K1 | TRIPPING-KED-23-00175 | 0242/20230324/002 | Kedah | Jitra | 11kV | Underground | 24-03-2023 02:42 | PPU KEPALA BATAS KB3 | P/E TMN NURI KJT19020 CB1 | P/E TMN NURI KJT19020 - | Core Opened | Partly Environment | Cable | TRANSIENT | 24-03-2023 02:52 | 24-03-2023 03:22 | 30 |  |  |  | 24-03-2023 04:22 | 1.67
Northern | K1 | TRIPPING-KED-23-00182 | 0242/20230326/082 | Kedah | Jitra | 11kV | Underground | 26-03-2023 23:12 | PPU CHANGLOON CL4 | PPU CHANGLOON CL4 | TMN JELUTONG FASA 2 KJT19192 - C/SUB TAMAN NAPOH KJT19292 | Core Opened | Defective Manufacture | Cable | CABLE | 26-03-2023 23:17 |  | 0 | 27-03-2023 21:43 | 29-03-2023 23:55 | 50 | 30-03-2023 01:04 | 73.87
Northern | K1 | TRIPPING-KED-23-00183 | 0242/20230327/023 | Kedah | Jitra | 11kV | Underground | 27-03-2023 07:36 | PPU LOJI AIR ARAU GIS 11K5 | PDB KLG BERAS PERING KJT01775 CB1 | PBT PIDA 12A KJT01336 - KLG FUTURE BIOMASS KJT19325 | Core Opened | Partly Environment | Cable | CABLE | 27-03-2023 08:15 | 27-03-2023 08:30 | 15 | 28-03-2023 01:27 | 30-03-2023 22:20 | 68 | 30-03-2023 22:55 | 87.32
Northern | K1 | TRIPPING-KED-23-00187 | 0242/20230328/004 | Kedah | Jitra | 11kV | Underground | 28-03-2023 07:09 | PPU DARULAMAN 4K5 | RUMAH KEDAI 50 UNIT KJT19301 CB1 |  | Core Opened | Defective Manufacture | Cable | TRANSIENT | 28-03-2023 07:11 | 28-03-2023 07:55 | 44 |  |  |  | 28-03-2023 07:56 | 0.78
Northern | K1 | TRIPPING-PLS-23-00016 | 2610/20230329/086 | Perlis | Perlis | 11kV | Underground | 29-03-2023 17:56 | PPU POLITEKNIK PAUH PERLIS 2 | PPU POLITEKNIK PAUH PERLIS CB2 | MRSM ULU PAUH KAN02114 - TMN KURUNG ANAI KAN02837 | Core Opened | Partly Environment | Cable | CABLE | 29-03-2023 18:02 | 29-03-2023 18:40 | 38 | 30-03-2023 22:02 | 05-04-2023 23:23 | 145 | 05-04-2023 23:35 | 173.65
Northern | K1 | TRIPPING-PLS-23-00018 | 2610/20230330/023 | Perlis | Perlis | 11kV | Underground | 30-03-2023 07:16 | PPU PADANG BESAR CB12 | PPU PADANG BESAR CB12 | PPU PADANG BESAR CB12 - PDB TIONG NAM KAN00014 | Core Opened | Defective Manufacture | Cable | CABLE | 30-03-2023 07:18 | 30-03-2023 07:23 | 5 | 31-03-2023 18:21 | 09-04-2023 23:37 | 221 | 09-04-2023 23:50 | 256.57
Northern | K1 | TRIPPING-PLS-23-00019 | 2610/20230330/035 | Perlis | Perlis | 11kV | Underground | 30-03-2023 08:25 | PPU PADANG BESAR CB10 | UKK PADANG BESAR KAN00047 CB1 | TPK PELUPUSAN SAMPAH RIMBA MAS KAN02824 - PBT CHECK POINT KAN00094 | Core Opened | Partly Environment | Cable | CABLE | 30-03-2023 09:15 | 30-03-2023 09:30 | 15 | 31-03-2023 18:20 | 06-04-2023 23:17 | 148 | 06-04-2023 23:28 | 183.05
Northern | K1 | TRIPPING-KED-23-00229 | 0242/20230409/031 | Kedah | Jitra | 11kV | Underground | 09-04-2023 17:17 | PMU BUKIT KAYU HITAM BKH4 | PMU BUKIT KAYU HITAM BKH4 | PDB PLUSWAY KJT01134 - PDB INFRA SG. LAKA NO 1 KJT01135 | Core Opened | Partly Environment | Cable | CABLE | 09-04-2023 17:27 | 09-04-2023 18:06 | 39 | 10-04-2023 01:32 | 11-04-2023 21:53 | 44 | 11-04-2023 22:21 | 53.07
Northern | K1 | TRIPPING-KED-23-00236 | 0242/20230412/003 | Kedah | Jitra | 11kV | Overhead | 12-04-2023 05:39 | PPU KEPALA BATAS KB3 | P/E TMN NURI KJT19020 CB1 | P/E TMN NURI KJT19020 - | Insulation Breakdown | Animal | Conductor | NO FAULT | 12-04-2023 05:43 | 12-04-2023 06:27 | 44 |  |  |  | 12-04-2023 07:56 | 2.28
Northern | K1 | TRIPPING-PLS-23-00020 | 2610/20230416/017 | Perlis | Perlis | 11kV | Underground | 16-04-2023 11:00 | PPU MINI PPU ABI 13 | PPU MINI PPU ABI CB13 | TMN MAS MUDA FASA 4 - PDB TMN AMAN | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 16-04-2023 11:20 | 16-04-2023 11:55 | 35 | 16-04-2023 22:21 | 01-05-2023 09:22 | 347 | 01-05-2023 09:42 | 358.7
Northern | K1 | TRIPPING-KED-23-00244 | 0245/20230417/003 | Kedah | Kuala Nerang | 11kV | Underground | 17-04-2023 01:32 | PPU NAKA 4K5 | PPU NAKA 4K5 | PPU NAKA 4K5 - PDB QTRS GURU NAKA KKN00361 | Core Opened | Partly Environment | Cable | CABLE | 17-04-2023 01:34 | 17-04-2023 02:08 | 34 | 17-04-2023 11:32 | 19-04-2023 03:51 | 40 | 19-04-2023 04:22 | 50.83
Northern | K1 | TRIPPING-PLS-23-00021 | 2610/20230417/026 | Perlis | Perlis | 11kV | Underground | 17-04-2023 14:16 | PMU CHUPING CB3 | PDB UITM ARAU KAN00863 CB1 | PDB UITM ARAU KAN00863 - PDB KLG BATA-KAN KAN00862 | Core Opened | Partly Environment | Cable | CABLE | 17-04-2023 14:45 | 17-04-2023 15:23 | 38 | 18-04-2023 23:09 | 28-04-2023 00:16 | 217 | 28-04-2023 00:24 | 250.13
Northern | K1 | TRIPPING-PLS-23-00022 | 2610/20230419/002 | Perlis | Perlis | 11kV | Underground | 19-04-2023 08:34 | PMU KANGAR CB1 | PDB SEKOLAH VOKASIONAL KANGAR KAN00472 | PDB SK SRI INDRA KAN00470 - PDB PERPUSTAKAAN NEGERI-PPNPS KAN00469 | Core Opened | Partly Environment | Cable | CABLE | 19-04-2023 08:59 | 19-04-2023 09:12 | 13 | 19-04-2023 23:17 | 26-04-2023 22:39 | 167 | 26-04-2023 22:50 | 182.27
Northern | K1 | TRIPPING-KED-23-00246 | 0242/20230419/008 | Kedah | Jitra | 11kV | Overhead | 19-04-2023 09:31 | PPU PELUBANG PL3 | PDB SK PENGHULU HJ DARUS KJT00700 | PBT KG. LEMBAH ARANG KJT18894 - SSL KUALA PAI KJT18893 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 19-04-2023 09:36 | 19-04-2023 10:17 | 41 | 19-04-2023 22:12 | 20-04-2023 18:39 | 20 | 20-04-2023 19:01 | 33.5
Northern | K1 | TRIPPING-KED-23-00248 | 0242/20230420/054 | Kedah | Jitra | 11kV | Overhead | 20-04-2023 15:35 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01798 CB1 | PBT KG. KUBANG PASU KJT00729 - PBT KBG BETONG KJT00736 | Snapped by Trees / Branches | Partly Environment | ABC Conductor | CABLE | 20-04-2023 15:37 | 20-04-2023 16:05 | 28 | 20-04-2023 17:18 | 21-04-2023 01:04 | 7 | 21-04-2023 01:34 | 9.98
Northern | K1 | TRIPPING-PLS-23-00023 | 2610/20230423/023 | Perlis | Perlis | 11kV | Underground | 23-04-2023 05:10 | PMU KUALA PERLIS CB10 | PDB TMN SEMARAK KAN00660 CB1 | PLB KLG HAI SOON KAN00668 - PDB BALAI BOMBA KUALA PERLIS KAN01905 | Core Opened | Defective Manufacture | Cable | CABLE | 23-04-2023 05:33 | 23-04-2023 05:55 | 22 | 23-04-2023 20:18 | 28-04-2023 23:03 | 122 | 28-04-2023 23:15 | 138.08
Northern | K1 | TRIPPING-KED-23-00254 | 0242/20230427/047 | Kedah | Jitra | 11kV | Underground | 27-04-2023 16:41 | PPU JERLUN SJ2 | PDB KLG PROSES UDANG KERPAN KJT01685 CB1 | PAT KG. GANDAI KJT01426 - PDB KLG PROSES UDANG KERPAN KJT01685 | Core Opened | Defective Manufacture | Cable | CABLE | 27-04-2023 16:44 | 27-04-2023 17:15 | 31 | 28-04-2023 00:44 | 29-04-2023 18:05 | 41 | 29-04-2023 18:56 | 50.25
Northern | K1 | TRIPPING-PLS-23-00024 | 2610/20230427/037 | Perlis | Perlis | 11kV | Underground | 27-04-2023 18:08 | PMU KUALA PERLIS CB5 | PMU KUALA PERLIS CB5 | PMU KUALA PERLIS CB5 - PLB LOT 764 TMN KUALA PERLIS KAN01180 | Core Opened | Defective Manufacture | Cable | CABLE | 27-04-2023 18:28 | 27-04-2023 18:48 | 20 | 28-04-2023 23:25 | 27-05-2023 17:18 | 689 | 27-05-2023 17:38 | 719.5
Northern | K1 | TRIPPING-PLS-23-00026 | 2610/20230427/044 | Perlis | Perlis | 11kV | Substation | 27-04-2023 18:09 | PMU KUALA PERLIS CB3 | PMU KUALA PERLIS CB3 | PDB WATER TREATMENT KAN01204 - PDB LOJI AIR SG. BARU KAN01142 | Dielectric | Dielectric Deterioration | RMU SF6 | CABLE | 27-04-2023 18:15 | 27-04-2023 18:45 | 30 | 10-05-2023 13:14 | 11-05-2023 01:11 | 11 | 11-05-2023 01:40 | 319.52
Northern | K1 | TRIPPING-PLS-23-00027 | 2610/20230427/038 | Perlis | Perlis | 11kV | Underground | 27-04-2023 18:11 | PMU KUALA PERLIS CB8 | PMU KUALA PERLIS CB8 |  | Core Opened | Defective Manufacture | Cable | TRANSIENT | 27-04-2023 18:16 | 27-04-2023 18:46 | 30 |  |  |  | 27-04-2023 21:07 | 2.93
Northern | K1 | TRIPPING-KED-23-00262 | 0245/20230429/030 | Kedah | Kuala Nerang | 11kV | Underground | 29-04-2023 20:13 | PPU KUALA NERANG 5K5 | PPU KUALA NERANG 5K5 | PLB RMU PPU KUALA NERANG KKN00565 - PDB TMN AKASIA KKN00579 | Core Opened | Partly Environment | Cable | CABLE | 29-04-2023 20:20 | 29-04-2023 20:58 | 38 | 30-04-2023 15:30 | 01-05-2023 20:40 | 29 | 01-05-2023 22:15 | 50.03
Northern | K1 | TRIPPING-PLS-23-00028 | 2610/20230501/036 | Perlis | Perlis | 11kV | Underground | 01-05-2023 19:25 | PMU KUALA PERLIS CB1 | PLB TOK KUNING 1 KAN00614 | SMK SERIAB KAN00612 - PLB BEHOR TEMAK KAN00611 | Core Opened | Partly Environment | Cable | CABLE | 01-05-2023 19:52 | 01-05-2023 20:29 | 37 | 02-05-2023 21:24 | 15-05-2023 01:29 | 292 | 15-05-2023 01:43 | 318.3
Northern | K1 | TRIPPING-PLS-23-00029 | RE/2610/20230502/PLS/00029 | Perlis | Perlis | 11kV | Underground | 02-05-2023 08:45 | PPU BUKIT KETERI 5K5 | PDB TMN SRI PUTERI KAN02605 | PDB TMN SRI PUTERI KAN00808 - |  |  |  | TRANSIENT | 02-05-2023 08:50 |  | 0 |  |  |  | 02-05-2023 09:42 | 0.95
Northern | K1 | TRIPPING-PLS-23-00030 | 2610/20230504/022 | Perlis | Perlis | 11kV | Underground | 04-05-2023 12:56 | PPU PADANG BESAR CB12 | RPA PADANG BESAR KAN02910 CB1 | RPA PADANG BESAR KAN02910 - KEM PGA NO 1 KAN02914 |  |  |  | CABLE | 04-05-2023 16:00 | 04-05-2023 16:44 | 44 | 06-05-2023 11:02 | 06-05-2023 21:27 | 10 | 06-05-2023 23:14 | 58.3
Northern | K1 | TRIPPING-KED-23-00282 | 0242/20230504/030 | Kedah | Jitra | 11kV | Underground | 04-05-2023 16:37 | PPU KODIANG KD2 | PDB SM TUNKU BENDAHARA KJT01260 CB1 | PBT KG. TOK ARANG 1 KJT01258 - PLB KG. PERING KJT01259 | Core Opened | Partly Environment | Cable | CABLE | 04-05-2023 16:39 | 04-05-2023 17:22 | 43 | 05-05-2023 21:45 | 06-05-2023 08:46 | 11 | 06-05-2023 09:29 | 40.87
Northern | K1 | TRIPPING-PLS-23-00032 | 2610/20230510/035 | Perlis | Perlis | 11kV | Underground | 10-05-2023 16:20 | PPU PADANG BESAR CB12 | RPA PADANG BESAR KAN02910 | RPA PADANG BESAR KAN02910 - KEM PGA NO 1 KAN02914 | Core Opened | Partly Environment | Cable | CABLE | 10-05-2023 16:45 | 10-05-2023 17:00 | 15 | 11-05-2023 17:48 | 13-05-2023 22:56 | 53 | 13-05-2023 23:18 | 78.97
Northern | K1 | TRIPPING-KED-23-00300 | 0242/20230510/080 | Kedah | Jitra | 11kV | Underground | 10-05-2023 22:38 | PPU CHANGLOON CL2 | PPU CHANGLOON CL2 | TMN MERBAU NO 2 KJT19330 - PDB TMN MERANTI-JITRA KJT01629 | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 10-05-2023 22:45 | 10-05-2023 23:30 | 45 | 11-05-2023 22:27 | 24-05-2023 18:03 | 307 | 25-05-2023 13:36 | 350.97
Northern | K1 | TRIPPING-KED-23-00311 | 0242/20230512/010 | Kedah | Jitra | 11kV | Underground | 12-05-2023 09:11 | PPU CHANGLOON CL3 | PPU CHANGLOON CL3 | PDB R/AWAM CHANGLUN KJT00970 - PLB PEKAN CHANGLUN 1 KJT00971 | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 12-05-2023 09:13 | 12-05-2023 09:46 | 33 | 13-05-2023 00:29 | 25-05-2023 12:12 | 299 | 25-05-2023 12:30 | 315.32
Northern | K1 | TRIPPING-KED-23-00318 | 0245/20230514/015 | Kedah | Kuala Nerang | 11kV | Underground | 14-05-2023 18:20 | PPU KUALA NERANG 3K5 | PPU KUALA NERANG 3K5 | PBT BUKIT NYAMOK KKN00235 - PBT SENA BAKONG 2 KKN00612 | Core Opened | Partly Environment | Cable | CABLE | 14-05-2023 18:23 | 14-05-2023 19:05 | 42 | 15-05-2023 18:35 | 19-05-2023 03:50 | 81 | 19-05-2023 04:58 | 106.63
Northern | K1 | TRIPPING-PLS-23-00033 | 2610/20230514/042 | Perlis | Perlis | 11kV | Substation | 14-05-2023 19:41 | PPU BUKIT KETERI 5K5 | PPU BUKIT KETERI 5K5 | PE MATRI KAN01395 - | Dielectric | Dielectric Deterioration | RMU SF6 | SWITCHGEAR | 14-05-2023 19:45 | 14-05-2023 20:20 | 35 | 28-05-2023 12:14 | 28-05-2023 23:49 | 11 | 29-05-2023 00:36 | 340.92
Northern | K1 | TRIPPING-PLS-23-00034 | 2610/20230515/086 | Perlis | Perlis | 11kV | Underground | 15-05-2023 22:18 | PMU KUALA PERLIS CB10 | PDB TMN SEMARAK KAN00658 CB1 | PDB TMN SEMARAK-KAN KAN00658 - PDB BALAI POLIS KAN00661 | Core Opened | Partly Environment | Cable | CABLE | 15-05-2023 22:20 | 15-05-2023 22:50 | 30 | 16-05-2023 20:15, 07-06-2023 12:30 | 07-06-2023 10:10, 07-06-2023 22:03 | 517, 9 | 08-06-2023 22:50 | 576.53
Northern | K1 | TRIPPING-PLS-23-00036 | 2610/20230516/148 | Perlis | Perlis | 11kV | Underground | 16-05-2023 11:14 | PPU LOJI AIR ARAU GIS 5K5 | PPU LOJI AIR ARAU GIS 5K5 | KOMPLEK TOK ARAU KAN02860 - PDB SK ARAU KAN00956 | Core Opened | Partly Environment | Cable | CABLE | 16-05-2023 11:33 | 16-05-2023 11:51 | 18 | 17-05-2023 21:34, 08-06-2023 11:36 | 07-06-2023 10:11, 08-06-2023 23:08 | 492, 11 | 08-06-2023 23:24 | 564.17
Northern | K1 | TRIPPING-PLS-23-00037 | 2610/20230522/055 | Perlis | Perlis | 11kV | Underground | 22-05-2023 19:47 | PPU SIMPANG EMPAT CB9 | PPU SIMPANG EMPAT CB9 | FUSE BLOW AT PDG BENTA - | Core Opened | Partly Environment | Cable | NO FAULT | 22-05-2023 19:49 | 22-05-2023 20:22 | 33 |  |  |  | 22-05-2023 21:15 | 1.47
Northern | K1 | TRIPPING-PLS-23-00039 | 2610/20230522/116 | Perlis | Perlis | 11kV | Underground | 22-05-2023 23:19 | PPU SHORUBBER CB8 | PDB KOMP KASTAM KANGAR KAN00497 CB1 | KOMPLEKS MATIN KAN02544 - PDB SMPG ABI KAN00313 | Core Opened | Partly Environment | Cable | CABLE | 22-05-2023 23:24 | 22-05-2023 23:48 | 24 | 24-05-2023 00:39 | 25-05-2023 21:19 | 44 | 25-05-2023 21:27 | 70.13
Northern | K1 | TRIPPING-PLS-23-00040 | 2610/20230524/009 | Perlis | Perlis | 11kV | Underground | 24-05-2023 04:52 | PMU KANGAR CB2 | PDB TELEKOM LAMA KANGAR KAN00551 CB1 | PDB BANDARAN(NOP) KAN00438 - PDB BUKIT LAGI NO.2 KAN01897 | Core Opened | Partly Environment | Cable | CABLE | 24-05-2023 05:01 | 24-05-2023 05:30 | 29 | 26-05-2023 21:29 | 01-06-2023 23:44 | 146 | 02-06-2023 00:30 | 211.63
Northern | K1 | TRIPPING-PLS-23-00041 | 2610/20230526/016 | Perlis | Perlis | 11kV | Underground | 26-05-2023 15:06 | PPU PADANG BESAR CB2 | PDB GUA KELAM PEKAN KAKI BUKIT KAN00134 | PDB BALAI POLIS PKN KAKI BUKIT KAN00136 - PDB PEKAN KAKI BUKIT KAN00137 |  |  |  | CABLE | 26-05-2023 17:13 | 26-05-2023 17:48 | 35 | 29-05-2023 17:35 | 29-05-2023 18:47 | 1 | 30-05-2023 17:23 | 98.28
Northern | K1 | TRIPPING-PLS-23-00042 | 2610/20230528/023 | Perlis | Perlis | 11kV | Underground | 28-05-2023 17:08 | PMU KUALA PERLIS CB12 | PDB DIBUK SYNERGY KAN01260 CB1 | PDB DIBUK SYNERGY KAN01260 - PDB 4 UNIT KLG KAN01276 | Core Opened | Partly Environment | Cable | CABLE | 28-05-2023 17:10 | 28-05-2023 17:54 | 44 | 30-05-2023 21:46 | 04-06-2023 09:03 | 107 | 04-06-2023 09:50 | 160.7
Northern | K1 | TRIPPING-PLS-23-00044 | 2610/20230609/003 | Perlis | Perlis | 11kV | Underground | 09-06-2023 03:43 | PPU SHORUBBER CB5 | BEHOR MENTALOON KAN00974 CB1 | PAT TELAGA HJ LATIF 1 KAN00994 - PBT KUBANG BODOH KAN00966 | Core Opened | Partly Environment | Cable | CABLE | 09-06-2023 04:04 | 09-06-2023 04:20 | 16 | 10-06-2023 21:32 | 18-06-2023 18:42 | 189 | 18-06-2023 18:43 | 231
Northern | K1 | TRIPPING-PLS-23-00046 | 2610/20230609/018 | Perlis | Perlis | 11kV | Substation | 09-06-2023 07:01 | PPU BUKIT KETERI 7K5 | PDB TMN BESERI JAYA KAN00176 |  | Dielectric breakdown | Shorted By Animal | HV Cable (Tx Tail) | TRANSIENT | 09-06-2023 07:08 | 09-06-2023 07:50 | 42 |  |  |  | 09-06-2023 08:11 | 1.17
Northern | K1 | TRIPPING-PLS-23-00047 | 2610/20230612/018 | Perlis | Perlis | 11kV | Underground | 12-06-2023 13:26 | PPU LOJI AIR ARAU GIS 6K5 | PPU LOJI AIR ARAU GIS 6K5 | SEK KEBANGSAAN JELEMPOK - PBT JELEMPOK, - PAT PADANG BIAK - PBT JELEMPOK | Core Opened | Partly Environment | Cable | CABLE, CABLE | 12-06-2023 13:35 | 12-06-2023 14:05 | 30 | 12-06-2023 17:47 | 12-06-2023 22:02 | 4 | 12-06-2023 22:24 | 8.97
Northern | K1 | TRIPPING-PLS-23-00048 | 2610/20230612/078 | Perlis | Perlis | 11kV | Underground | 12-06-2023 22:34 | PPU PADANG BESAR CB12 | RPA PADANG BESAR KAN02910 | RPA PADANG BESAR KAN02910 - KEM PGA NO 1 KAN02914 |  |  |  | CABLE | 12-06-2023 21:00 | 12-06-2023 21:35 | 35 |  |  |  | 16-06-2023 09:25 | 82.85
Northern | K1 | TRIPPING-KED-23-00378 | 0242/20230613/033 | Kedah | Jitra | 11kV | Underground | 13-06-2023 18:37 | PPU CHANGLOON CL2 | PPU CHANGLOON CL2 |  | Core Opened | Defective Manufacture | Cable | TRANSIENT | 13-06-2023 18:58 | 13-06-2023 19:18 | 20 |  |  |  | 13-06-2023 20:50 | 2.22
Northern | K1 | TRIPPING-PLS-23-00049 | RE/2610/20230614/PLS/00049 | Perlis | Perlis | 11kV | Underground | 14-06-2023 07:46 | PMU KUALA PERLIS CB7 | PDB PANGSAPURI KG.WAI KAN02713 | PDB PANGSAPURI KG.WAI KAN02713 - |  |  |  | NO FAULT | 14-06-2023 07:55 | 14-06-2023 08:35 | 40 |  |  |  | 15-06-2023 22:02 | 38.27
Northern | K1 | TRIPPING-PLS-23-00050 | 2610/20230619/022 | Perlis | Perlis | 11kV | Underground | 19-06-2023 12:58 | PPU PADANG BESAR CB12 | RPA PADANG BESAR KAN02911 CB1 | PAT KG. MELAYU KAN02803 - |  |  |  | CABLE | 19-06-2023 13:40 | 19-06-2023 14:07 | 27 | 19-06-2023 15:37 | 19-06-2023 16:45 | 1 | 19-06-2023 16:47 | 3.82
Northern | K1 | TRIPPING-PLS-23-00051 | 2610/20230624/051 | Perlis | Perlis | 11kV | Underground | 24-06-2023 22:04 | PPU LOJI AIR ARAU GIS 4K5 | PPU LOJI AIR ARAU GIS 4K5 | PBT KG. SENA KAN00928 - PLB PADANG TELELA KAN00927 | Core Opened | Partly Environment | Cable | CABLE | 24-06-2023 22:15 | 24-06-2023 22:30 | 15 | 25-06-2023 21:01 | 21-07-2023 22:59 | 625 | 21-07-2023 23:11 | 649.12
Northern | K1 | TRIPPING-KED-23-00397 | 0242/20230625/012 | Kedah | Jitra | 11kV | Underground | 25-06-2023 13:06 | PPU UUM SINTOK ST6 | PDB ASRAMA UUM KJT01743 CB1 | SSD AKADEMI BINAAN MALAYSIA KJT01024 - PDB QTRS UUM SINTOK 1 KJT01025 | Core Opened | Partly Environment | Cable | CABLE | 25-06-2023 13:15 | 25-06-2023 13:40 | 25 | 25-06-2023 22:24 | 26-06-2023 22:54 | 24 | 27-06-2023 23:29 | 58.38
Northern | K1 | TRIPPING-KED-23-00403 | 0242/20230628/003 | Kedah | Jitra | 11kV | Overhead | 28-06-2023 08:52 | PPU KEPALA BATAS KB3 | P/E TMN NURI KJT19020 CB1 | S/S KG PADANG KJT00585 - | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | TRANSIENT | 28-06-2023 09:03 | 28-06-2023 09:30 | 27 |  |  |  | 28-06-2023 10:52 | 2
Northern | K1 | TRIPPING-KED-23-00404 | 0242/20230628/065 | Kedah | Jitra | 11kV | Underground | 28-06-2023 21:35 | PMU TANJUNG PAUH TP19 | PMU TANJUNG PAUH TP19 | PDB PEKAN JITRA 2A KJT00375 - PDB PEKAN JITRA 2B KJT00376 | Core Opened | Partly Environment | Cable | CABLE | 28-06-2023 21:36 | 28-06-2023 22:00 | 24 | 29-06-2023 22:26 | 04-07-2023 03:13 | 100 | 04-07-2023 03:30 | 125.92
Northern | K1 | TRIPPING-KED-23-00411 | 0242/20230702/001 | Kedah | Jitra | 11kV | Underground | 02-07-2023 01:11 | PPU CHANGLOON CL4 | PDB MRSM JITRA KJT00953 CB1 | PDB PUSAT BELIA JITRA KJT00958 - PBT KG. SALIT KJT00959 | Core Opened | Defective Manufacture | Cable | CABLE | 02-07-2023 01:13 | 02-07-2023 01:45 | 32 | 02-07-2023 22:19, 03-07-2023 16:45 | 03-07-2023 10:23, 03-07-2023 23:51 | 12, 7 | 04-07-2023 00:21 | 47.17
Northern | K1 | TRIPPING-KED-23-00429 | 0242/20230708/032 | Kedah | Jitra | 11kV | Underground | 08-07-2023 22:57 | PPU JERLUN SJ6 | PPU JERLUN SJ6 | PPU JERLUN SJ6 - | Dielectric breakdown | Shorted By Animal | HV Cable (Tx Tail) | NO FAULT | 08-07-2023 23:00 | 08-07-2023 23:30 | 30 |  |  |  | 09-07-2023 01:54 | 2.95
Northern | K1 | TRIPPING-PLS-23-00052 | 2610/20230709/007 | Perlis | Perlis | 11kV | Underground | 09-07-2023 03:38 | PMU KUALA PERLIS CB1 | PDB AMAN FISHMEAL KAN00623 CB1 | SMK SERIAB KAN00612 - PLB BEHOR TEMAK KAN00611 | Core Opened | Defective Manufacture | Cable | CABLE | 09-07-2023 03:41 | 09-07-2023 04:05 | 24 | 09-07-2023 22:54 | 15-07-2023 00:31 | 121 | 15-07-2023 00:43 | 141.08
Northern | K1 | TRIPPING-PLS-23-00053 | 2610/20230709/043 | Perlis | Perlis | 11kV | Underground | 09-07-2023 13:24 | PPU SIMPANG EMPAT CB4 | PPU SIMPANG EMPAT CB4 | PLB BUNGA EMAS -RB17 KAN01078 - PAT BUNGA EMAS TENGAH KAN01096 | Core Opened | Partly Environment | Cable | CABLE | 09-07-2023 13:29 | 09-07-2023 14:10 | 41 | 22-07-2023 10:56 | 22-07-2023 21:10 | 10 | 22-07-2023 21:25 | 320.02
Northern | K1 | TRIPPING-KED-23-00434 | 0242/20230709/080 | Kedah | Jitra | 11kV | Underground | 09-07-2023 15:13 | PPU UUM SINTOK ST6 | PDB ASRAMA UUM KJT01743 CB1 | SS BUKIT DAMAR KKN00598 - SSD RUMAH PAM GENTING IBAI KKN00594 | Core Opened | Partly Environment | Cable | CABLE | 09-07-2023 15:17 | 09-07-2023 15:50 | 33 | 09-07-2023 22:49 | 12-07-2023 02:11 | 51 | 12-07-2023 02:28 | 59.25
Northern | K1 | TRIPPING-PLS-23-00054 | 2610/20230710/017 | Perlis | Perlis | 11kV | Underground | 10-07-2023 12:08 | PMU CHUPING CB6 | PMU CHUPING CB6 | PDB KOK KELANG 2 KAN00251 - PAT KOK KELANG 1-VVIP KAN00252 | Core Opened | Defective Manufacture | Cable | CABLE | 10-07-2023 12:10 | 10-07-2023 12:35 | 25 | 16-07-2023 10:10 | 16-07-2023 22:12 | 12 | 16-07-2023 22:28 | 154.33
Northern | K1 | TRIPPING-KED-23-00441 | 0242/20230711/039 | Kedah | Jitra | 11kV | Underground | 11-07-2023 21:44 | PPU UUM SINTOK ST5 | PPU UUM SINTOK ST5 | PDB KLJ PERTANIAN KJT01605 - S/S KLJ PERTANIAN BKT TANGGA KJT01847 | Core Opened | Partly Environment | Cable | CABLE | 11-07-2023 21:44 | 11-07-2023 22:28 | 44 | 12-07-2023 16:30, 12-07-2023 18:19 | 12-07-2023 18:17, 13-07-2023 17:07 | 1, 22 | 13-07-2023 17:25 | 43.68
Northern | K1 | TRIPPING-PLS-23-00055 | 2610/20230712/006 | Perlis | Perlis | 11kV | Underground | 12-07-2023 11:26 | PMU CHUPING CB10 | PMU CHUPING CB10 | PMU CHUPING CB10 - PDB UITM ARAU KAN02053 | Core Opened | Defective Manufacture | Cable | CABLE | 12-07-2023 11:36 | 12-07-2023 12:18 | 42 | 15-07-2023 18:02, 01-08-2023 10:20 | 22-07-2023 22:31, 01-08-2023 16:50 | 172, 6 | 01-08-2023 17:10 | 485.73
Northern | K1 | TRIPPING-KED-23-00444 | 0242/20230713/008 | Kedah | Jitra | 11kV | Underground | 13-07-2023 09:34 | PPU JERLUN SJ6 | PPU JERLUN SJ6 | SMK PMTG.BONGLAI KJT01518 - PLB PIDA 3 TUNJANG KJT01519 | Core Opened | Partly Environment | Cable | CABLE | 13-07-2023 09:36 | 13-07-2023 10:20 | 44 | 13-07-2023 21:47 | 15-07-2023 22:20 | 48 | 15-07-2023 22:50 | 61.27
Northern | K1 | TRIPPING-KED-23-00451 | 0242/20230715/208 | Kedah | Jitra | 11kV | Underground | 15-07-2023 11:04 | PMU BUKIT KAYU HITAM BKH4 | PMU BUKIT KAYU HITAM BKH4 | PDB PROTAB AGROBASE KJT01138 - PDB INFRA SG. LAKA NO 1 KJT01137 | Core Opened | Defective Manufacture | Cable | CABLE | 15-07-2023 11:08 | 15-07-2023 11:32 | 24 | 15-07-2023 23:47 | 20-07-2023 23:14 | 119 | 20-07-2023 23:45 | 132.68
Northern | K1 | TRIPPING-PLS-23-00056 | 2610/20230716/089 | Perlis | Perlis | 11kV | Underground | 16-07-2023 13:13 | PMU CHUPING CB1 | PLB KAJI CUACA KAN00789 | PLB TMN 20 KAN00777 - P/E SEK KEB DATO KAYAMAN KAN02547 | Core Opened | Partly Environment | Cable | CABLE | 16-07-2023 13:20 | 16-07-2023 13:40 | 20 | 17-07-2023 21:19, 26-07-2023 13:49 | 22-07-2023 22:33, 27-07-2023 08:35 | 121, 18 | 27-07-2023 09:01 | 259.8
Northern | K1 | TRIPPING-PLS-23-00058 | 2610/20230725/027 | Perlis | Perlis | 11kV | Underground | 25-07-2023 10:25 | PMU KANGAR CB1 | PDB SEKOLAH VOKASIONAL KANGAR KAN00472 CB1 | PDB PERPUSTAKAAN NEGERI-PPNPS KAN00468 - PDB HOSPITAL KANGAR KAN00455 | Core Opened | Partly Environment | Cable | CABLE | 25-07-2023 10:28 | 25-07-2023 11:19 | 51 | 25-07-2023 22:45, 15-08-2023 15:12 | 26-07-2023 08:14, 16-08-2023 00:19 | 9, 9 | 16-08-2023 00:43 | 518.3
Northern | K1 | TRIPPING-KED-23-00472 | 0242/20230726/002 | Kedah | Jitra | 11kV | Substation | 26-07-2023 00:35 | PPU CHANGLOON CL3 | A/R SG KELIAN KJT00982 |  | Dielectric breakdown | Shorted By Animal | HV Cable (Tx Tail) | NO FAULT | 26-07-2023 00:45 | 26-07-2023 01:00 | 15 |  |  |  | 26-07-2023 01:15 | 0.67
Northern | K1 | TRIPPING-PLS-23-00059 | 2610/20230727/013 | Perlis | Perlis | 11kV | Underground | 27-07-2023 05:24 | PMU KANGAR CB6 | PMU KANGAR CB6 | VETERINAR KANGAR KAN02975 - MAHKAMAH BARU KAN03109 | Core Opened | Partly Environment | Cable | CABLE | 27-07-2023 05:30 | 27-07-2023 05:45 | 15 | 27-07-2023 22:09, 28-07-2023 15:28 | 28-07-2023 08:24, 15-08-2023 08:51 | 10, 425 | 16-08-2023 19:29 | 494.08
Northern | K1 | TRIPPING-KED-23-00479 | 0245/20230729/001 | Kedah | Kuala Nerang | 11kV | Underground | 29-07-2023 06:06 | PPU NAKA 4K5 | PDB BDR BARU NAKA KKN00375 | PLB KG. BELUKAR LUAS KKN00389 - PBT KG. DATOK KKN00391 | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 29-07-2023 06:13 | 29-07-2023 06:43 | 30 | 29-07-2023 18:01 | 31-07-2023 22:21 | 52 | 31-07-2023 23:10 | 65.07
Northern | K1 | TRIPPING-PLS-23-00060 | 2610/20230801/035 | Perlis | Perlis | 11kV | Underground | 01-08-2023 12:41 | PPU SHORUBBER CB5 | BEHOR MENTALOON KAN00975 | SK RAJA(P) BUDRIAH-VVIP KAN02307 - PAT LAHAR JAMBU KAN01011 | Core Opened | Partly Environment | Cable | CABLE | 01-08-2023 12:47 | 01-08-2023 13:30 | 43 | 06-08-2023 11:42 | 06-08-2023 21:24 | 9 | 06-08-2023 21:38 | 128.95
Northern | K1 | TRIPPING-PLS-23-00061 | RE/2610/20230801/PLS/00061 | Perlis | Perlis | 11kV | Underground | 01-08-2023 13:18 | PPU BUKIT KETERI 5K5 | PDB TMN SRI PUTERI KAN02605 | RE(RSO) OUTREACH GREEN 1 B1 - |  |  |  | CABLE | 01-08-2023 13:30 | 01-08-2023 13:50 | 20 |  |  |  | 03-08-2023 22:50 | 57.53
Northern | K1 | TRIPPING-PLS-23-00062 | 2610/20230804/101 | Perlis | Perlis | 11kV | Underground | 04-08-2023 11:22 | PMU KUALA PERLIS CB5 | PMU KUALA PERLIS CB5 | PBT KG. TELOK KAN01820 - KLG AIS IGLOO KAN02066 | Core Opened | Partly Environment | Cable | CABLE | 04-08-2023 11:30 | 04-08-2023 11:49 | 19 | 04-08-2023 20:39 | 11-08-2023 22:45 | 170 | 11-08-2023 22:59 | 179.62
Northern | K1 | TRIPPING-KED-23-00500 | 0245/20230805/005 | Kedah | Kuala Nerang | 11kV | Overhead | 05-08-2023 04:38 | PPU KUALA NERANG 1K5 | A/R TG SEBERANG AR | PAT LENGKONG PEDU KKN00832 - PBT SS BULUH BESAR KKN00339 | Insulation Burnt | Partly Environment | Straight Through Joint | CABLE | 05-08-2023 06:02 | 05-08-2023 06:16 | 14 | 05-08-2023 14:20 | 06-08-2023 16:23 | 26 | 06-08-2023 17:05 | 36.45
Northern | K1 | TRIPPING-KED-23-00506 | 0242/20230809/004 | Kedah | Jitra | 11kV | Underground | 09-08-2023 09:01 | PPU JERLUN SJ6 | PPU JERLUN SJ6 | PAT PIDA 4 TUNJANG KJT01513 - PBT TALIAIR 4 TUNJANG KJT01512 | Core Opened | Defective Manufacture | Cable | CABLE | 09-08-2023 09:19 | 09-08-2023 09:41 | 22 | 09-08-2023 22:49 | 13-08-2023 22:21 | 95 | 13-08-2023 23:14 | 110.22
Northern | K1 | TRIPPING-PLS-23-00063 | 2610/20230815/014 | Perlis | Perlis | 11kV | Underground | 15-08-2023 14:53 | PPU UNIMAP GIS 2K5 | PPU UNIMAP GIS 2K5 | PPU UNIMAP GIS 2K5 - FELDA CHUPING NO.2 KAN02680 | Core Opened | Partly Environment | Cable | CABLE | 15-08-2023 14:58 | 15-08-2023 15:42 | 44 | 16-08-2023 18:24 | 23-08-2023 21:30 | 171 | 23-08-2023 21:41 | 198.8
Northern | K1 | TRIPPING-PLS-23-00064 | 2610/20230816/042 | Perlis | Perlis | 11kV | Underground | 16-08-2023 11:54 | PPU PADANG BESAR CB10 | PDB BATU BERTANGKUP KAN00097 CB1 | PDB BATU BERTANGKUP KAN00097 - RIMBUNAN KASEH-KAN KAN03150 | Core Opened | Partly Environment | Cable | CABLE | 16-08-2023 12:03 | 16-08-2023 12:14 | 11 | 17-08-2023 15:40, 21-08-2023 12:10 | 21-08-2023 09:19, 21-08-2023 21:42 | 89, 9 | 21-08-2023 21:55 | 130.02
Northern | K1 | TRIPPING-PLS-23-00065 | 2610/20230818/003 | Perlis | Perlis | 11kV | Underground | 18-08-2023 07:16 | PPU PADANG BESAR CB2 | FISHING NET KAN00068 |  | Core Opened | Defective Manufacture | Cable | TRANSIENT | 18-08-2023 07:43 | 18-08-2023 08:10 | 27 |  |  |  | 18-08-2023 09:05 | 1.82
Northern | K1 | TRIPPING-PLS-23-00066 | 2610/20230823/004 | Perlis | Perlis | 11kV | Underground | 23-08-2023 03:05 | PMU KANGAR CB16 | SSU GIANT KGAR KAN02771 CB1 | HTL SRI MALAYSIA KANGAR KAN02047 - SSU SUK N.PERLIS KAN03137 | Core Opened | Partly Environment | Cable | CABLE | 23-08-2023 03:17 | 23-08-2023 03:51 | 34 | 23-08-2023 22:34 | 02-09-2023 00:27 | 217 | 02-09-2023 00:51 | 237.77
Northern | K1 | TRIPPING-KED-23-00526 | 0242/20230823/019 | Kedah | Jitra | 11kV | Underground | 23-08-2023 11:10 | PPU JERLUN SJ6 | PPU JERLUN SJ6 | PATOD SEMATANG JAWA KJT01501 - PBT PIDA 5 PMTG BONGLAI KJT01500 | Core Opened | Partly Environment | Cable | CABLE | 23-08-2023 11:15 | 23-08-2023 11:46 | 31 | 23-08-2023 12:57 | 23-08-2023 21:55 | 8 | 23-08-2023 22:22 | 11.2
Northern | K1 | TRIPPING-PLS-23-00067 | 2610/20230823/036 | Perlis | Perlis | 11kV | Underground | 23-08-2023 14:26 | PPU PADANG BESAR CB11 | PPU PADANG BESAR CB11 | PDB HALAL HUB KAN02416 - SK FELDA RIMBA MAS KAN02414 | Core Opened | Partly Environment | Cable | CABLE | 23-08-2023 14:30 | 23-08-2023 15:12 | 42 | 24-08-2023 22:02, 14-09-2023 20:03, 17-09-2023 11:11 | 31-08-2023 18:19, 17-09-2023 08:40, 17-09-2023 23:23 | 164, 60, 12 | 17-09-2023 23:37 | 609.18
Northern | K1 | TRIPPING-PLS-23-00068 | 2610/20230825/002 | Perlis | Perlis | 11kV | Underground | 25-08-2023 00:57 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 | CSU RUMAH PAM JEJAWI KAN03190 - PAT BEHOR GELAM KAN00980 | Core Opened | Partly Environment | Cable | CABLE | 25-08-2023 00:59 | 25-08-2023 01:35 | 36 | 25-08-2023 21:26 | 03-09-2023 23:25 | 217 | 03-09-2023 23:38 | 238.68
Northern | K1 | TRIPPING-KED-23-00533 | 0242/20230828/005 | Kedah | Jitra | 11kV | Underground | 28-08-2023 03:45 | PPU JERLUN SJ6 | PPU JERLUN SJ6 | PPU JERLUN SJ6 - PATOD AIR HITAM KJT01483 | Core Opened | Defective Manufacture | Cable | CABLE | 28-08-2023 04:10 | 28-08-2023 04:40 | 30 | 28-08-2023 21:51 | 31-08-2023 16:26 | 66 | 31-08-2023 17:16 | 85.52
Northern | K1 | TRIPPING-PLS-23-00070 | 2610/20230829/054 | Perlis | Perlis | 11kV | Underground | 29-08-2023 23:53 | PMU KANGAR CB7 | HOSPITAL TUANKU FAUZIAH KAN02619 | HOSPITAL TUANKU FAUZIAH KAN02619 - TMN BUNGA PADI KAN00387 | Core Opened | Defective Manufacture | Cable | CABLE | 29-08-2023 23:55 | 30-08-2023 00:25 | 30 | 31-08-2023 18:26, 09-09-2023 11:39 | 09-09-2023 10:09, 10-09-2023 00:54 | 207, 13 | 10-09-2023 01:10 | 265.28
Northern | K1 | TRIPPING-KED-23-00538 | 0242/20230830/061 | Kedah | Jitra | 11kV | Underground | 30-08-2023 21:17 | PPU DARULAMAN 10K5 | PPU DARULAMAN 10K5 | PDB TMN RASA SAYANG KJT00442 - PAT CHIP SENG HENG KJT00443 | Core Opened | Partly Environment | Cable | CABLE | 30-08-2023 21:20 | 30-08-2023 21:48 | 28 | 31-08-2023 23:14 | 03-09-2023 22:07 | 70 | 03-09-2023 22:51 | 97.57
Northern | K1 | TRIPPING-PLS-23-00071 | 2610/20230904/001 | Perlis | Perlis | 11kV | Substation | 04-09-2023 02:11 | PPU SIMPANG EMPAT CB1 | PDB KLG PADI MAJU KAN01041 CB1 | PAT PADANG PETANI KAN01049 - | Terminal Shorted by Animal / Insects | Partly Environment | Jumper to Drop Out Fuse Wire | NO FAULT | 04-09-2023 02:13 | 04-09-2023 02:49 | 36 |  |  |  | 04-09-2023 03:15 | 1.07
Northern | K1 | TRIPPING-PLS-23-00072 | 2610/20230906/004 | Perlis | Perlis | 11kV | Underground | 06-09-2023 05:54 | PMU KUALA PERLIS CB8 | PMU KUALA PERLIS CB8 | PDB FRIENDLY WAY FROZEN KAN01266 - PDB INDUSTRI MARA (KIM) KAN01828 | Core Opened | Defective Manufacture | Cable | CABLE | 06-09-2023 06:03 | 06-09-2023 06:47 | 44 | 17-09-2023 10:41 | 18-09-2023 01:28 | 14 | 18-09-2023 01:44 | 283.83
Northern | K1 | TRIPPING-PLS-23-00073 | 2610/20230908/015 | Perlis | Perlis | 11kV | Underground | 08-09-2023 11:38 | PPU BUKIT KETERI 7K5 | PDB TMN BESERI JAYA KAN00176 | PLB GUAR JENTIK KAN00172 - P/E ALUR LIMPAH BARAT KAN02725 | Core Opened | Partly Environment | Cable | CABLE | 08-09-2023 11:44 | 08-09-2023 12:25 | 41 | 08-09-2023 20:35, 20-09-2023 11:28 | 09-09-2023 08:37, 20-09-2023 22:03 | 12, 10 | 20-09-2023 10:06 | 286.47
Northern | K1 | TRIPPING-KED-23-00562 | 0242/20230911/031 | Kedah | Jitra | 11kV | Underground | 11-09-2023 13:05 | PMU TANJUNG PAUH TP19 | PMU TANJUNG PAUH TP19 | KOMPLEK PERNIAGAAN AMAN KJT19164 - PDB TMN JITRA JAYA KJT00437 | Core Opened | Partly Environment | Cable | CABLE | 11-09-2023 13:09 | 11-09-2023 13:29 | 20 | 11-09-2023 22:23 | 13-09-2023 21:04 | 46 | 13-09-2023 21:27 | 56.37
Northern | K1 | TRIPPING-KED-23-00570 | 0242/20230914/030 | Kedah | Jitra | 11kV | Underground | 14-09-2023 20:25 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00895 CB1 | PATOD HOSBA KJT00908 - PLB TMN SRI HOSBA KJT00902, - PDB PERINDUSTRIAN KEDA BIJAL KJT00922 - PDB PERUMAHAN KEDA BINJAL KJT00921 | Core Opened | Partly Environment | Cable | CABLE, CABLE | 14-09-2023 20:40 |  | 0 | 15-09-2023 23:07, 16-09-2023 00:41 | 19-09-2023 21:07, 17-09-2023 18:38 | 94, 41 | 19-09-2023 21:30 | 121.08
Northern | K1 | TRIPPING-KED-23-00571 | 0245/20230915/003 | Kedah | Kuala Nerang | 11kV | Overhead | 15-09-2023 02:24 | PPU KUALA NERANG 7K5 | PPU KUALA NERANG 7K5 | LOJI AIR KUALA NERANG 2 KKN00747 - PEJ DAERAH BARU KKN00519 | Insulation Breakdown | Insulation Deterioration | Conductor | CABLE | 15-09-2023 02:39 |  | 0 | 15-09-2023 12:18 | 19-09-2023 23:23 | 107 | 20-09-2023 00:42 | 118.3
Northern | K1 | TRIPPING-KED-23-00572 | 0242/20230915/017 | Kedah | Jitra | 11kV | Underground | 15-09-2023 02:51 | PPU DARULAMAN 3K5 | KLG MAKANAN&MINUMAN JLN B.WANG KJT18990 CB1 | PAT KG. BIAK-ALS KJT00252 - RUMAH PAM PAYA TOK TEH KJT19185 | Core Opened | Partly Environment | Cable | CABLE | 15-09-2023 04:20 | 15-09-2023 04:29 | 9 | 16-09-2023 00:42 | 18-09-2023 21:09 | 68 | 18-09-2023 21:46 | 90.92
Northern | K1 | TRIPPING-PLS-23-00074 | 2610/20230917/006 | Perlis | Perlis | 11kV | Underground | 17-09-2023 09:31 | PMU KUALA PERLIS CB8 | PMU KUALA PERLIS CB8 | PDB FRIENDLY WAY FROZEN KAN01265 - | Dielectric breakdown | Dielectric Deterioration | Cable PILC | TRANSIENT | 17-09-2023 09:44 | 17-09-2023 09:49 | 5 |  |  |  | 17-09-2023 10:38 | 1.12
Northern | K1 | TRIPPING-KED-23-00583 | 0242/20230918/037 | Kedah | Jitra | 11kV | Underground | 18-09-2023 22:14 | PMU BUKIT KAYU HITAM BKH4 | PDB PROTAB AGROBASE KJT01138 | PAT BATU 26 KJT19463 - SSD NO.1 KJT00824 | Core Opened | Partly Environment | Cable | CABLE | 18-09-2023 22:34 | 18-09-2023 23:10 | 36 | 20-09-2023 00:41 | 22-09-2023 00:39 | 47 | 22-09-2023 00:58 | 74.73
Northern | K1 | TRIPPING-PLS-23-00075 | 2610/20230919/006 | Perlis | Perlis | 11kV | Underground | 19-09-2023 09:36 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 | CSU RUMAH PAM JEJAWI KAN03190 - PAT BEHOR GELAM KAN00980 | Core Opened | Partly Environment | Cable | CABLE | 19-09-2023 09:38 | 19-09-2023 10:02 | 24 | 20-09-2023 22:46 | 23-09-2023 22:10 | 71 | 23-09-2023 22:17 | 108.68
Northern | K1 | TRIPPING-KED-23-00588 | 0245/20230921/002 | Kedah | Kuala Nerang | 11kV | Underground | 21-09-2023 03:25 | PPU KUALA NERANG 1K5 | PLB TANJUNG SEBERANG KKN00287 | PBT SS BULUH BESAR KKN00339 - PAT LENGKONG PEDU KKN00832 | Core Opened | Defective Manufacture | Cable | CABLE | 21-09-2023 04:32 | 21-09-2023 04:45 | 13 | 21-09-2023 13:20 | 29-09-2023 21:01 | 199 | 29-09-2023 23:21 | 211.93
Northern | K1 | TRIPPING-KED-23-00590 | 0242/20230921/063 | Kedah | Jitra | 11kV | Underground | 21-09-2023 22:19 | PMU BUKIT KAYU HITAM BKH4 | PMU BUKIT KAYU HITAM BKH4 | PDB PROTAB AGROBASE KJT01140 - SSD NO.1 KJT01141 | Core Opened | Partly Environment | Cable | CABLE | 21-09-2023 22:25 | 21-09-2023 22:54 | 29 | 22-09-2023 22:36 | 25-09-2023 21:26 | 70 | 25-09-2023 22:16 | 95.95
Northern | K1 | TRIPPING-KED-23-00591 | 0242/20230922/012 | Kedah | Jitra | 11kV | Overhead | 22-09-2023 09:28 | PPU LOJI AIR ARAU GIS 11K5 | PPU LOJI AIR ARAU GIS 11K5 | PPU LOJI AIR ARAU GIS 11K5 - PLB TALIAIR 2 PERING KJT01379 | Core Opened | Partly Environment | Cable | CABLE | 22-09-2023 09:32 | 22-09-2023 10:15 | 43 | 22-09-2023 22:38 | 23-09-2023 22:35 | 23 | 24-09-2023 22:40 | 61.2
Northern | K1 | TRIPPING-PLS-23-00076 | 2610/20230922/037 | Perlis | Perlis | 11kV | Underground | 22-09-2023 23:04 | PMU KUALA PERLIS CB8 | PMU KUALA PERLIS CB8 | PDB KRAF TANGAN KAN00672 - PDB TMN BUMITA KAN00596 | Core Opened | Partly Environment | Cable | CABLE | 22-09-2023 23:08 |  | 0 | 24-09-2023 22:23, 19-10-2023 21:44 | 19-10-2023 12:31, 20-10-2023 11:22 | 590, 13 | 20-10-2023 11:33 | 660.48
Northern | K1 | TRIPPING-PLS-23-00077 | 2610/20230924/050 | Perlis | Perlis | 11kV | Underground | 24-09-2023 21:33 | PMU KANGAR CB2 | PDB TELEKOM LAMA KANGAR KAN00548 CB1 | PDB TELEKOM LAMA KANGAR KAN00548 - HOSPITAL TUANKU FAUZIAH KAN02622 | Core Opened | Partly Environment | Cable | CABLE | 24-09-2023 21:33 | 24-09-2023 21:55 | 22 | 25-09-2023 21:21 | 07-10-2023 01:02 | 267 | 07-10-2023 01:26 | 291.88
Northern | K1 | TRIPPING-PLS-23-00078 | 2610/20230927/007 | Perlis | Perlis | 11kV | Substation | 27-09-2023 08:33 | PPU BUKIT KETERI 7K5 | PDB TMN BESERI JAYA KAN00176 CB1 |  | Terminal Shorted by Animal / Insects | Partly Environment | Jumper to Drop Out Fuse Wire | TRANSIENT | 27-09-2023 08:42 | 27-09-2023 09:02 | 20 |  |  |  | 27-09-2023 09:00 | 0.45
Northern | K1 | TRIPPING-KED-23-00621 | 0242/20231001/013 | Kedah | Jitra | 11kV | Underground | 01-10-2023 11:40 | PPU CHANGLOON CL2 | PPU CHANGLOON CL2 | PDB TMN MERANTI-JITRA KJT01629 - TMN MERBAU NO 2 KJT19330 | Failed, Shorted by Water Ingress | Partly Environment | Straight Through Joint | CABLE | 01-10-2023 11:43 | 01-10-2023 12:05 | 22 | 01-10-2023 22:23 | 03-10-2023 22:24 | 48 | 03-10-2023 23:05 | 59.42
Northern | K1 | TRIPPING-PLS-23-00079 | 2610/20231001/028 | Perlis | Perlis | 11kV | Underground | 01-10-2023 14:02 | PMU KUALA PERLIS CB8 | PMU KUALA PERLIS CB8 | PDB FRIENDLY WAY FROZEN KAN01266 - PDB INDUSTRI MARA (KIM) KAN01828 | Core Opened | Partly Environment | Cable | CABLE | 01-10-2023 14:03 | 01-10-2023 14:40 | 37 | 05-10-2023 10:53 | 05-10-2023 22:13 | 11 | 05-10-2023 22:28 | 104.43
Northern | K1 | TRIPPING-PLS-23-00080 | 2610/20231001/032 | Perlis | Perlis | 11kV | Underground | 01-10-2023 14:02 | PMU KUALA PERLIS CB3 | PMU KUALA PERLIS CB3 | PDB LOJI AIR SG. BARU KAN01143 - PDT RUMAH PAM SMPG EMPAT KAN01144 | Core Opened | Partly Environment | Cable | CABLE | 01-10-2023 14:05 | 01-10-2023 14:41 | 36 | 08-10-2023 09:09 | 08-10-2023 22:13 | 13 | 08-10-2023 22:45 | 176.72
Northern | K1 | TRIPPING-PLS-23-00081 | 2610/20231001/039 | Perlis | Perlis | 11kV | Underground | 01-10-2023 14:02 | PMU KUALA PERLIS CB11 | PDB KUALA PERLIS KAN01164 CB1 | TMN UTARA JAYA K.PERLIS-VVIP KAN01197 - PAT PADANG BESAR SELATAN KAN01208 | Core Opened | Partly Environment | Cable | CABLE |  |  | 0 | 02-10-2023 21:48 | 07-10-2023 23:06 | 121 | 07-10-2023 23:23 | 153.35
Northern | K1 | TRIPPING-PLS-23-00082 | 2610/20231002/007 | Perlis | Perlis | 11kV | Underground | 02-10-2023 10:56 | PMU KANGAR CB5 | PVCB REPOH CERIA-VVIP KAN02632 CB1 | PVCB RPA SANTAN 2 KAN02465 - PLB PADANG LATI KAN00771 | Core Opened | Partly Environment | Cable | CABLE | 02-10-2023 10:58 | 02-10-2023 11:30 | 32 | 14-10-2023 09:19 | 14-10-2023 20:58 | 11 | 14-10-2023 21:15 | 298.32
Northern | K1 | TRIPPING-PLS-23-00083 | 2610/20231008/003 | Perlis | Perlis | 11kV | Underground | 08-10-2023 00:25 | PMU KANGAR CB2 | PDB TELEKOM LAMA KANGAR KAN00551 CB1 | PLB BEHOR TEMAK KAN00609 - TMN BEHOR TEMAK JAYA KAN01907 | Core Opened | Partly Environment | Cable | CABLE | 08-10-2023 00:44 | 08-10-2023 01:05 | 21 | 09-10-2023 21:36 | 24-10-2023 22:24 | 360 | 24-10-2023 22:35 | 406.17
Northern | K1 | TRIPPING-KED-23-00633 | 0242/20231010/029 | Kedah | Jitra | 11kV | Underground | 10-10-2023 21:36 | PPU UUM SINTOK ST6 | PPU UUM SINTOK ST6 | PPU UUM SINTOK ST6 - PDB ASRAMA UUM KJT01019 | Core Opened | Partly Environment | Cable | CABLE |  |  | 0 | 11-10-2023 01:07 | 12-10-2023 18:40 | 41 | 12-10-2023 19:18 | 45.7
Northern | K1 | TRIPPING-KED-23-00648 | 0242/20231015/003 | Kedah | Jitra | 11kV | Underground | 15-10-2023 04:52 | PMU BUKIT KAYU HITAM BKH2 | PMU BUKIT KAYU HITAM BKH2 | PMU BUKIT KAYU HITAM BKH2 - PDB NO. 5 KJT01130 | Core Opened | Partly Environment | Cable | CABLE | 15-10-2023 05:11 | 15-10-2023 05:55 | 44 | 16-10-2023 00:19 | 18-10-2023 21:29 | 69 | 18-10-2023 22:59 | 90.12
Northern | K1 | TRIPPING-PLS-23-00084 | 2610/20231016/003 | Perlis | Perlis | 11kV | Underground | 16-10-2023 02:08 | PMU KANGAR CB5 | PVCB REPOH CERIA-VVIP KAN02632 CB1 | PLB PADANG LATI KAN00771 - PVCB RPA SANTAN 2 KAN02465 | Core Opened | Partly Environment | Cable | CABLE | 16-10-2023 02:15 | 16-10-2023 02:48 | 33 | 16-10-2023 21:31 | 26-10-2023 08:15 | 226 | 26-10-2023 08:23 | 246.25
Northern | K1 | TRIPPING-KED-23-00652 | 0242/20231016/021 | Kedah | Jitra | 11kV | Underground | 16-10-2023 16:53 | PMU BUKIT KAYU HITAM BKH5 | PMU BUKIT KAYU HITAM BKH5 | PMU BUKIT KAYU HITAM BKH5 - TMN NILAM MAKMUR KJT19227 | Core Opened | Defective Manufacture | Cable | CABLE | 16-10-2023 16:55 | 16-10-2023 18:01 | 66 | 17-10-2023 00:28 | 18-10-2023 21:36 | 45 | 18-10-2023 23:01 | 54.13
Northern | K1 | TRIPPING-KED-23-00657 | 0245/20231017/012 | Kedah | Kuala Nerang | 11kV | Underground | 17-10-2023 23:04 | PPU KUALA NERANG 4K5 | PPU KUALA NERANG 4K5 | PPU KUALA NERANG 4K5 - PDB TELEKOM KUALA NERANG KKN00001 | Insulation Burnt | Partly Environment | Cable Termination | CABLE | 17-10-2023 23:06 | 17-10-2023 23:40 | 34 | 18-10-2023 13:05 | 20-10-2023 00:23 | 35 | 20-10-2023 00:50 | 49.77
Northern | K1 | TRIPPING-KED-23-00670 | 0242/20231021/001 | Kedah | Jitra | 11kV | Overhead | 21-10-2023 07:53 | PPU KODIANG KD5 | PPU KODIANG KD5 | SK PUTAT KJT01670 - PBT ALOR TOK CHIK KJT01749 | Insulation Burnt | Partly Environment | Cable Termination | CABLE | 21-10-2023 08:03 | 21-10-2023 08:30 | 27 | 21-10-2023 22:36 | 26-10-2023 22:01 | 119 | 26-10-2023 22:51 | 134.97
Northern | K1 | TRIPPING-KED-23-00673 | 0245/20231022/011 | Kedah | Kuala Nerang | 11kV | Underground | 22-10-2023 12:14 | PPU NAKA 5K5 | PDB KEDA KG. BUKIT KAS02717 CB1 | PLB KG. BUKIT JLN NAKA KKN00459 - KILANG BERAS MIHODA NO.2 KKN00759 | Insulation Failed, Shorted by Water Ingress | Partly Environment | Cable | CABLE | 22-10-2023 12:29 | 22-10-2023 12:58 | 29 | 22-10-2023 17:28 | 24-10-2023 21:44 | 52 | 24-10-2023 21:56 | 57.7
Northern | K1 | TRIPPING-KED-23-00696 | 0242/20231101/082 | Kedah | Jitra | 11kV | Underground | 01-11-2023 18:25 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00895 CB1 | PDB PERUMAHAN KEDA BINJAL KJT00921 - PDB PERINDUSTRIAN KEDA BIJAL KJT00922KG BONGKOK SANTAN KAN02814 - PAT TASIK MELATI KAN00774 | Core Opened | Defective Manufacture | Cable | CABLE | 01-11-2023 18:29 | 01-11-2023 18:50 | 21 | 01-11-2023 21:14 | 04-11-2023 22:22 | 73 | 04-11-2023 22:55 | 76.5
Northern | K1 | TRIPPING-PLS-23-00090 | 2610/20231102/001 | Perlis | Perlis | 11kV | Underground | 02-11-2023 00:58 | PMU KANGAR CB5 | PVCB RPA SANTAN 2 KAN02468 CB1 | PDB LEBUH RAYA SERIAB KAN00600 - QTRS POLIS-KAN KAN00601 | Core Opened | Partly Environment | Cable | CABLE | 02-11-2023 00:58 | 02-11-2023 01:40 | 42 | 15-11-2023 10:15 | 15-11-2023 22:14 | 11 | 15-11-2023 22:31 | 333.55
Northern | K1 | TRIPPING-PLS-23-00091 | 2610/20231103/001 | Perlis | Perlis | 11kV | Underground | 03-11-2023 04:48 | PMU KUALA PERLIS CB8 | PDB TMN BUMITA KAN00598 CB1 | STN SUIS KG. LANGSAT KJT00859 - CS REBAN AYAM KG LANGSAT KJT19199 | Core Opened | Defective Manufacture | Cable | CABLE | 03-11-2023 04:49 | 03-11-2023 05:18 | 29 | 03-11-2023 21:00 | 24-11-2023 14:20 | 497 | 24-11-2023 14:30 | 513.7
Northern | K1 | TRIPPING-KED-23-00714 | 0242/20231104/038 | Kedah | Jitra | 11kV | Underground | 04-11-2023 19:30 | PPU CHANGLOON CL2 | PDB TMN MERBAU KJT01859 CB1 | PBT PADANG ASUN KJT18958 - PBT PAYA KEMUNTING ESTATE KJT00947 | Core Opened | Partly Environment | Cable | CABLE | 04-11-2023 19:53 | 04-11-2023 20:35 | 42 | 05-11-2023 17:25 | 07-11-2023 19:12 | 49 | 07-11-2023 20:40 | 73.17
Northern | K1 | TRIPPING-KED-23-00720 | 0242/20231106/021 | Kedah | Jitra | 11kV | Underground | 06-11-2023 14:30 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00895 | PAT RUMAH PAM JALAN KODIANG KJT00990 - PLD FELDA BATU 8 CHANGLUN KJT19116 | Core Opened | Partly Environment | Cable | CABLE | 06-11-2023 14:57 |  | 0 | 06-11-2023 22:05, 11-11-2023 17:49 | 11-11-2023 17:16, 11-11-2023 18:30 | 115, 0 | 11-11-2023 18:53 | 124.38
Northern | K1 | TRIPPING-KED-23-00724 | 0242/20231107/048 | Kedah | Jitra | 11kV | Underground | 07-11-2023 17:43 | PPU CHANGLOON CL3 | PPU CHANGLOON CL3 | BT 20 RUMAH PAM KAN00081 - PLB FELDA MATA AIR 1 KAN00085 | Core Opened | Partly Environment | Cable | CABLE | 07-11-2023 17:47 | 07-11-2023 18:25 | 38 | 08-11-2023 22:36 | 14-11-2023 21:40 | 143 | 14-11-2023 22:01 | 172.3
Northern | K1 | TRIPPING-PLS-23-00093 | 2610/20231110/025 | Perlis | Perlis | 11kV | Underground | 10-11-2023 14:14 | PPU PADANG BESAR CB2 | FISHING NET KAN00068 |  | Core Opened | Defective Manufacture | Cable | CABLE | 10-11-2023 14:36 |  | 0 | 11-11-2023 22:09 | 16-11-2023 22:11 | 120 | 16-11-2023 22:28 | 152.23
Northern | K1 | TRIPPING-PLS-23-00094 | 2610/20231112/002 | Perlis | Perlis | 11kV | Underground | 12-11-2023 08:04 | PPU PADANG BESAR CB9 | PPU PADANG BESAR CB9 | PDB BANGUNAN KESELAMATAN UUM - SS PUSAT PEMBANGUNAN EKS UUM KJT01034 | Core Opened | Partly Environment | Cable | NO FAULT | 12-11-2023 08:15 | 12-11-2023 08:55 | 40 |  |  |  | 12-11-2023 09:39 | 1.58
Northern | K1 | TRIPPING-KED-23-00739 | 0242/20231112/046 | Kedah | Jitra | 11kV | Underground | 12-11-2023 21:27 | PPU UUM SINTOK ST6 | PDB ASRAMA UUM KJT01743 CB1 | PDB SM JENAN KJT00559 - | Core Opened | Defective Manufacture | Cable | CABLE | 12-11-2023 21:34 | 12-11-2023 22:05 | 31 | 13-11-2023 22:24 | 23-11-2023 18:04 | 235 | 23-11-2023 18:38 | 261.18
Northern | K1 | TRIPPING-KED-23-00740 | 0242/20231113/006 | Kedah | Jitra | 11kV | Substation | 13-11-2023 08:54 | PMU TANJUNG PAUH TP9 | KOMERSIAL SQUARE KOLEJ HEIGHT KJT19376 | PADAT LADANG AYAM KG BAROKHAS KKN00783 - | Dielectric |  | RMU SF6 | SWITCHGEAR | 13-11-2023 09:26 | 13-11-2023 09:48 | 22 | 18-11-2023 21:14 | 19-11-2023 23:02 | 25 | 20-11-2023 00:05 | 159.18
Northern | K1 | TRIPPING-KED-23-00743 | 0245/20231114/003 | Kedah | Kuala Nerang | 11kV | Underground | 14-11-2023 08:12 | PPU NAKA 3K5 | PPU NAKA 3K5 | PDB PERUMAHAN KEDA BINJAL KJT00921 - PDB PERINDUSTRIAN KEDA BIJAL KJT00922 | Insulation Breakdown | Contamination | Cable Termination | TRANSIENT | 14-11-2023 08:24 | 14-11-2023 08:45 | 21 |  |  |  | 14-11-2023 11:00 | 2.8
Northern | K1 | TRIPPING-KED-23-00744 | 0242/20231114/015 | Kedah | Jitra | 11kV | Underground | 14-11-2023 09:28 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00895 CB1 | PAT RUMAH PAM JALAN KODIANG - PLD FELDA BATU 8 CHANGLUN KJT19116 | Core Opened | Partly Environment | Cable | CABLE | 14-11-2023 09:45 | 14-11-2023 10:10 | 25 | 14-11-2023 22:05 | 16-11-2023 17:42 | 43 | 16-11-2023 18:05 | 56.62
Northern | K1 | TRIPPING-KED-23-00753 | 0242/20231121/003 | Kedah | Jitra | 11kV | Underground | 21-11-2023 02:55 | PPU CHANGLOON CL3 | PPU CHANGLOON CL3 |  | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 21-11-2023 03:11 | 21-11-2023 03:38 | 27 | 21-11-2023 22:20 | 27-11-2023 11:02 | 132 | 27-11-2023 11:18 | 152.38
Northern | K1 | TRIPPING-KED-23-00758 | 0242/20231122/023 | Kedah | Jitra | 11kV | Substation | 22-11-2023 18:22 | PMU TANJUNG PAUH TP19 | PMU TANJUNG PAUH TP19 | PDB TMN SEMATANG JAYA - PPU SHORUBBER CB10 | Dielectric | Dielectric Deterioration | RMU SF6 | NO FAULT | 22-11-2023 18:25 | 22-11-2023 19:03 | 38 |  |  |  | 22-11-2023 19:25 | 1.05
Northern | K1 | TRIPPING-PLS-23-00095 | 2610/20231124/010 | Perlis | Perlis | 11kV | Underground | 24-11-2023 12:34 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 | SK AGAMA ISLAMIAH BOHOR MALI - PBT BOHOR MALI KAN01156 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 24-11-2023 12:45 |  | 0 | 02-12-2023 10:52 | 02-12-2023 22:28 | 11 | 02-12-2023 22:45 | 202.18
Northern | K1 | TRIPPING-PLS-23-00096 | 2610/20231125/001 | Perlis | Perlis | 11kV | Underground | 25-11-2023 00:07 | PPU SIMPANG EMPAT CB9 | PPU SIMPANG EMPAT CB9 | PDB BALAI BOMBA KUALA PERLIS KAN01904 - PDB KRAF TANGAN KAN00669 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 25-11-2023 00:10 | 25-11-2023 00:40 | 30 | 25-11-2023 20:30 | 03-12-2023 17:55 | 189 | 03-12-2023 18:10 | 210.05
Northern | K1 | TRIPPING-PLS-23-00098 | 2610/20231127/042 | Perlis | Perlis | 11kV | Underground | 27-11-2023 23:06 | PMU KUALA PERLIS CB8 | PMU KUALA PERLIS CB8 | PDB PERUMAHAN KEDA BINJAL KJT00921 - PERINDUSTRIAN KEDA BINJAL KJT00922 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 27-11-2023 23:18 | 27-11-2023 23:40 | 22 | 28-11-2023 21:34, 11-12-2023 10:37 | 30-11-2023 10:45, 12-12-2023 00:26 | 37, 13 | 12-12-2023 00:45 | 337.65
Northern | K1 | TRIPPING-KED-23-00780 | 0242/20231201/027 | Kedah | Jitra | 11kV | Underground | 01-12-2023 19:40 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00895 CB1 | PDB TMN TUNKU MAHERAN 1 - PLB KEM BATALION 1 KJT01657 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 01-12-2023 19:42 | 01-12-2023 20:25 | 43 | 02-12-2023 21:01 | 09-12-2023 22:14 | 169 | 09-12-2023 22:44 | 195.07
Northern | K1 | TRIPPING-KED-23-00790 | 0242/20231208/016 | Kedah | Jitra | 11kV | Underground | 08-12-2023 16:03 | PMU TANJUNG PAUH TP6 | PMU TANJUNG PAUH TP6 | PDB PROCESSING FACTORY KAN00626 - PDB AMAN FISHMEAL KAN00624 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE, CABLE | 08-12-2023 16:08 | 08-12-2023 17:10 | 62 | 08-12-2023 17:29, 08-12-2023 22:19 | 08-12-2023 17:49, 11-12-2023 00:20 | 0, 50 | 11-12-2023 00:41 | 56.63
Northern | K1 | TRIPPING-PLS-23-00100 | 2610/20231209/001 | Perlis | Perlis | 11kV | Underground | 09-12-2023 02:46 | PMU KUALA PERLIS CB1 | PMU KUALA PERLIS CB1 | PBT KG. SURAU-KAN - PATOD UJUNG BATU KAN01069 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 09-12-2023 02:53 | 09-12-2023 03:09 | 16 | 10-12-2023 17:10 | 29-12-2023 18:18 | 457 | 29-12-2023 18:49 | 496.05
Northern | K1 | TRIPPING-PLS-23-00101 | 2610/20231209/064 | Perlis | Perlis | 11kV | Underground | 09-12-2023 13:52 | PPU SIMPANG EMPAT CB3 | PPU SIMPANG EMPAT CB3 | PAT PIDA 4 TUNJANG KJT01513 - | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 09-12-2023 14:06 | 09-12-2023 14:15 | 9 | 09-12-2023 14:54, 16-12-2023 10:37 | 09-12-2023 15:21, 16-12-2023 20:58 | 0, 10 | 16-12-2023 21:25 | 175.55
Northern | K1 | TRIPPING-KED-23-00792 | 0242/20231210/037 | Kedah | Jitra | 11kV | Overhead | 10-12-2023 18:03 | PPU JERLUN SJ6 | PPU JERLUN SJ6 | PDB PERUMAHAN KEDA BINJAL KJT00921 - PDB PERINDUSTRIAN KEDA BIJAL KJT00922 | Insulation Breakdown | Insulation Deterioration | Cable Termination | TRANSIENT | 10-12-2023 18:13 | 10-12-2023 18:50 | 37 |  |  |  | 10-12-2023 19:10 | 1.12
Northern | K1 | TRIPPING-KED-23-00806 | 0242/20231216/002 | Kedah | Jitra | 11kV | Underground | 16-12-2023 07:28 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00895 CB1 | PAT CHANGKAT TOK RAHMAN KJT00092 - PBT PIDA 1 KJT00091 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 16-12-2023 07:30 | 16-12-2023 07:55 | 25 | 17-12-2023 03:07, 21-12-2023 11:29 | 17-12-2023 04:19, 21-12-2023 23:29 | 1, 12 | 21-12-2023 23:43 | 136.25
Northern | K1 | TRIPPING-KED-23-00808 | 0242/20231216/048 | Kedah | Jitra | 11kV | Underground | 16-12-2023 13:16 | PPU JERLUN SJ6 | PPU JERLUN SJ6 | PIDA 1 - CHANGKAT TOK RAHMAN | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 16-12-2023 13:20 | 16-12-2023 13:55 | 35 | 16-12-2023 14:01, 17-12-2023 04:23, 23-12-2023 11:20 | 16-12-2023 14:11, 17-12-2023 11:33, 23-12-2023 21:40 | 0, 7, 10 | 23-12-2023 22:10 | 176.9
Northern | K1 | TRIPPING-PLS-23-00102 | RE/2610/20231216/PLS/00102 | Perlis | Perlis | 11kV | Underground | 16-12-2023 18:40 | PMU KUALA PERLIS CB13 | PMU KUALA PERLIS CB13 | PLB TMN 20 KAN00776 - PLB TMN EMAS-KAN KAN00289 |  |  |  | NO FAULT | 16-12-2023 19:00 | 16-12-2023 19:32 | 32 |  |  |  | 16-12-2023 19:45 | 1.08
Northern | K1 | TRIPPING-PLS-23-00103 | 2610/20231217/010 | Perlis | Perlis | 11kV | Underground | 17-12-2023 18:05 | PMU CHUPING CB1 | PLB KAJI CUACA KAN00789 | PDB LLM WANG TEPUS KJT00670 - PDB TMN MAHSURI FASA 2A KJT00671 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 17-12-2023 18:51 | 17-12-2023 19:10 | 19 | 18-12-2023 18:22, 03-01-2024 10:19 | 03-01-2024 09:36, 03-01-2024 21:39 | 375, 11 | 03-01-2024 21:50 | 411.75
Northern | K1 | TRIPPING-KED-23-00814 | 0242/20231218/002 | Kedah | Jitra | 11kV | Underground | 18-12-2023 06:59 | PMU TANJUNG PAUH TP14 | PMU TANJUNG PAUH TP14 | PDB RUMAH PAM JKR KAN00243 - PDB FELDA CHUPING 1 KAN00244 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 18-12-2023 07:05 | 18-12-2023 07:30 | 25 | 18-12-2023 22:47, 26-12-2023 09:46 | 19-12-2023 11:15, 26-12-2023 22:38 | 12, 12 | 26-12-2023 23:00 | 208.02
Northern | K1 | TRIPPING-PLS-23-00104 | 2610/20231228/032 | Perlis | Perlis | 11kV | Underground | 28-12-2023 23:41 | PPU UNIMAP GIS 2K5 | FELDA CHUPING NO.2 KAN02702 CB1 | PAT RUMAH PAM JALAN KODIANG KJT00990 - PLD FELDA BATU 8 CHANGLUN KJT19116 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 29-12-2023 00:12 | 29-12-2023 00:40 | 28 | 15-01-2024 11:18 | 15-01-2024 22:54 | 11 | 15-01-2024 23:09 | 431.47
Northern | K1 | TRIPPING-KED-23-00838 | 0242/20231229/049 | Kedah | Jitra | 11kV | Underground | 29-12-2023 21:06 | PPU CHANGLOON CL3 | PPU CHANGLOON CL3 | PDB KLG BAJA MK HOSBA KJT01692 - PDT YUNG HENG POULTRY KJT19442 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 29-12-2023 21:16 | 29-12-2023 21:32 | 16 | 30-12-2023 22:19, 01-01-2024 10:01 | 31-12-2023 14:13, 03-01-2024 00:21 | 15, 38 | 03-01-2024 01:00 | 99.9
Northern | K1 | TRIPPING-KED-23-00839 | 0242/20231230/038 | Kedah | Jitra | 11kV | Underground | 30-12-2023 22:34 | PPU KODIANG KD1 | SSBT RUMAH PAM PERING KJT01634 CB1 | PAT KUBANG JULOK KKN00370 - | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 30-12-2023 22:47 | 30-12-2023 23:20 | 33 | 31-12-2023 22:36, 03-01-2024 11:18 | 01-01-2024 20:53, 06-01-2024 21:36 | 22, 82 | 06-01-2024 21:50 | 167.27
Northern | K1 | TRIPPING-KED-24-00009 | 0245/20240103/001 | Kedah | Kuala Nerang | 11kV | Substation | 03-01-2024 08:18 | PPU NAKA 4K5 | PPU NAKA 4K5 | PPU DARULAMAN 3K5 - TMN PULASAN 2 KJT19316 | Possible Animal | NA | Transient | TRANSIENT | 03-01-2024 08:21 | 03-01-2024 08:55 | 34 |  |  |  | 03-01-2024 09:55 | 1.62
Northern | K1 | TRIPPING-KED-24-00014 | 0242/20240104/070 | Kedah | Jitra | 11kV | Underground | 04-01-2024 10:58 | PPU DARULAMAN 3K5 | PPU DARULAMAN 3K5 | PDB TMN SRI NYIOR KJT00032 - PDB SM P/NYIOR KJT00031 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 04-01-2024 11:02 | 04-01-2024 11:33 | 31 | 04-01-2024 15:44 | 04-01-2024 18:49 | 3 | 04-01-2024 20:56 | 9.97
Northern | K1 | TRIPPING-KED-24-00015 | 0242/20240104/071 | Kedah | Jitra | 11kV | Underground | 04-01-2024 11:01 | PPU DARULAMAN 4K5 | RUMAH KEDAI 50 UNIT KJT19301 CB1 | PDB SRI PERLIS INN KAN00505 - PDB SEKOLAH VOKASIONAL KANGAR KAN00474 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 04-01-2024 11:01 |  | 0 | 05-01-2024 22:05, 10-01-2024 11:03 | 06-01-2024 10:40, 10-01-2024 22:15 | 12, 11 | 10-01-2024 23:10 | 156.15
Northern | K1 | TRIPPING-PLS-24-00001 | 2610/20240104/020 | Perlis | Perlis | 11kV | Underground | 04-01-2024 16:28 | PPU SHORUBBER CB7 | PDB TMN HARMONI KANGAR KAN01924 | PLB TMN SRI UTAMA-ALS KJT00070 - TMN JITRA KJT00171 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 04-01-2024 16:30 | 04-01-2024 16:46 | 16 | 10-01-2024 09:46 | 10-01-2024 21:47 | 12 | 10-01-2024 21:57 | 149.48
Northern | K1 | TRIPPING-KED-24-00025 | 0242/20240108/017 | Kedah | Jitra | 11kV | Underground | 08-01-2024 04:46 | PPU DARULAMAN 9K5 | PPU DARULAMAN 9K5 | PDB SRI PERLIS INN KAN00505 - PDB SEKOLAH VOKASIONAL KANGAR KAN00474 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 08-01-2024 05:07 | 08-01-2024 05:15 | 8 | 09-01-2024 22:23, 11-01-2024 11:16 | 09-01-2024 23:02, 11-01-2024 18:47 | 0, 7 | 11-01-2024 19:51 | 87.08
Northern | K1 | TRIPPING-PLS-24-00002 | 2610/20240117/015 | Perlis | Perlis | 11kV | Underground | 17-01-2024 09:38 | PPU SHORUBBER CB7 | PDB TMN HARMONI KANGAR KAN01924 CB1 | PBT DRIVING RANGE KJT00212 - PDB TMN GOLF NO4 KJT00213 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 17-01-2024 09:39 | 17-01-2024 10:01 | 22 | 19-01-2024 17:44 | 20-01-2024 22:34 | 28 | 20-01-2024 22:46 | 85.13
Northern | K1 | TRIPPING-KED-24-00044 | 0242/20240120/002 | Kedah | Jitra | 11kV | Underground | 20-01-2024 07:18 | PPU DARULAMAN 8K5 | PPU DARULAMAN 8K5 | LOJI AIR PADANG SANAI 2 KKN00866 - RUMAH PAM AIR MENTAH KKN00533 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 20-01-2024 07:34 | 20-01-2024 07:45 | 11 | 20-01-2024 20:26 | 21-01-2024 00:21 | 3 | 21-01-2024 00:55 | 17.62
Northern | K1 | TRIPPING-KED-24-00045 | 0245/20240120/004 | Kedah | Kuala Nerang | 11kV | Overhead | 20-01-2024 14:54 | PPU MINI PPU L/AIR PDG SANAI LA3 | PPU MINI PPU L/AIR PDG SANAI LA3 | PBT DRIVING RANGE KJT00211 - | Open Circuit | Improper Installation | Straight Through Joint | CABLE | 20-01-2024 15:00 | 20-01-2024 15:25 | 25 | 20-01-2024 23:13 | 21-01-2024 22:24 | 23 | 21-01-2024 22:50 | 31.93
Northern | K1 | TRIPPING-KED-24-00046 | 0242/20240121/052 | Kedah | Jitra | 11kV | Substation | 21-01-2024 01:04 | PPU DARULAMAN 8K5 | PPU DARULAMAN 8K5 | PDB KLG IRICHI KAN01263 - PDB FRIENDLY WAY FROZEN KAN01264 | Dielectric | Dielectric Deterioration | RMU SF6 | SWITCHGEAR | 21-01-2024 01:06 | 21-01-2024 01:11 | 5 | 23-01-2024 11:10, 29-01-2024 11:18 | 24-01-2024 21:28, 30-01-2024 01:09 | 34, 13 | 30-01-2024 03:31 | 218.45
Northern | K1 | TRIPPING-PLS-24-00003 | 2610/20240122/002 | Perlis | Perlis | 11kV | Underground | 22-01-2024 06:38 | PMU KUALA PERLIS CB11 | PDB DIBUK SYNERGY KAN01259 CB1 | PATOD UJUNG BATU KAN01069 - PBT KG. SURAU-KAN KAN01070 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 22-01-2024 06:43 |  | 0 | 22-01-2024 22:07 | 29-01-2024 23:04 | 168 | 29-01-2024 23:19 | 184.68
Northern | K1 | TRIPPING-PLS-24-00004 | 2610/20240122/030 | Perlis | Perlis | 11kV | Underground | 22-01-2024 14:48 | PPU SIMPANG EMPAT CB3 | PPU SIMPANG EMPAT CB3 | STN SUIS 11KV IKBN JITRA KJT18896 - | Open Circuit | Soil Movement | Cable XLPE | CABLE | 22-01-2024 15:02 | 22-01-2024 15:20 | 18 | 29-01-2024 23:26 | 30-01-2024 22:21 | 22 | 30-01-2024 22:31 | 199.72
Northern | K1 | TRIPPING-KED-24-00050 | 0242/20240123/001 | Kedah | Jitra | 11kV | Underground | 23-01-2024 00:05 | PPU DARULAMAN 10K5 | STN SUIS 11KV IKBN JITRA KJT18896 CB1 | PPU KUALA NERANG 6K5 - PBT KG. BENDANG RAJA KKN00822 | Open Circuit | Soil Movement | Cable XLPE | NO FAULT | 23-01-2024 01:04 | 23-01-2024 01:25 | 21 |  |  |  | 23-01-2024 02:35 | 2.5
Northern | K1 | TRIPPING-KED-24-00051 | 0245/20240123/003 | Kedah | Kuala Nerang | 11kV | Overhead | 23-01-2024 10:18 | PPU KUALA NERANG 6K5 | PPU KUALA NERANG 6K5 | SK SG. BARU KAN02334 - PDB LOJI AIR SG. BARU KAN01141 | Insulation Breakdown | Insulation Deterioration | Conductor | CABLE | 23-01-2024 10:30 | 23-01-2024 10:40 | 10 | 23-01-2024 21:35 | 26-01-2024 20:46 | 71 | 26-01-2024 21:16 | 82.97
Northern | K1 | TRIPPING-PLS-24-00005 | 2610/20240124/009 | Perlis | Perlis | 11kV | Underground | 24-01-2024 08:21 | PPU SIMPANG EMPAT CB7 | PPU SIMPANG EMPAT CB7 | PBT PIDA 1 KJT00091 - PAT CHANGKAT TOK RAHMAN KJT00092 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 24-01-2024 08:23 | 24-01-2024 09:00 | 37 | 26-01-2024 21:24 | 31-01-2024 21:59 | 120 | 31-01-2024 22:30 | 182.15
Northern | K1 | TRIPPING-KED-24-00053 | 0242/20240124/025 | Kedah | Jitra | 11kV | Underground | 24-01-2024 13:36 | PPU JERLUN SJ6 | PPU JERLUN SJ6 | PDB KOMP AGAMA ISLAM KAN00522 - PDB TMN TOK PELUKA KAN00537 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 24-01-2024 13:40 | 24-01-2024 14:10 | 30 | 24-01-2024 23:03 | 27-01-2024 21:48 | 70 | 27-01-2024 21:57 | 80.35
Northern | K1 | TRIPPING-PLS-24-00006 | 2610/20240125/008 | Perlis | Perlis | 11kV | Underground | 25-01-2024 10:40 | PMU KANGAR CB10 | PDB FLAT POLIS KANGAR KAN00518 CB1 | PDB TMN MAHSURI FASA 2D KJT00613 - PDB TMN SUASANA DAMAI KJT00614 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 25-01-2024 11:36 | 25-01-2024 11:40 | 4 | 01-02-2024 11:43 | 02-02-2024 00:17 | 12 | 02-02-2024 00:32 | 181.87
Northern | K1 | TRIPPING-KED-24-00056 | 0242/20240126/021 | Kedah | Jitra | 11kV | Underground | 26-01-2024 22:42 | PMU TANJUNG PAUH TP21 | PDB TMN MAHSURI FASA 2D KJT00613 CB1 | PDB STN KERETAPI BUKIT KETERI KAN02511 - PBT GUAR PANJI KAN00213 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 26-01-2024 22:50 | 26-01-2024 23:24 | 34 | 27-01-2024 23:31 | 29-01-2024 18:28 | 42 | 30-01-2024 03:31 | 76.82
Northern | K1 | TRIPPING-PLS-24-00007 | 2610/20240127/018 | Perlis | Perlis | 11kV | Underground | 27-01-2024 21:51 | PPU BUKIT KETERI 3K5B | PVCB PANGGAS KAN00281 CB1 | PBT SS BULUH BESAR KKN00339 - PAT LENGKONG PEDU KKN00832 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 27-01-2024 21:54 | 27-01-2024 22:30 | 36 | 04-02-2024 10:11 | 04-02-2024 21:38 | 11 | 04-02-2024 21:52 | 192.02
Northern | K1 | TRIPPING-KED-24-00062 | 0245/20240129/010 | Kedah | Kuala Nerang | 11kV | Overhead | 29-01-2024 14:27 | PPU KUALA NERANG 1K5 | PPU KUALA NERANG 1K5 | LDG SG SERAYA KKN00772 - PDB LOJI AIR PADANG SANAI KKN00318 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 29-01-2024 14:32 | 29-01-2024 14:48 | 16 | 29-01-2024 21:42 | 31-01-2024 20:46 | 47 | 31-01-2024 21:55 | 55.47
Northern | K1 | TRIPPING-KED-24-00063 | 0245/20240129/016 | Kedah | Kuala Nerang | 11kV | Underground | 29-01-2024 20:48 | PPU MINI PPU L/AIR PDG SANAI LA3 | PPU MINI PPU L/AIR PDG SANAI LA3 | PDB SM TENGKU SULAIMAN - POLIKLINIK BESERI-VVIP KAN00302 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 29-01-2024 21:00 | 29-01-2024 21:15 | 15 | 29-01-2024 21:47 | 02-02-2024 02:21 | 76 | 02-02-2024 03:11 | 78.38
Northern | K1 | TRIPPING-PLS-24-00008 | 2610/20240203/066 | Perlis | Perlis | 11kV | Underground | 03-02-2024 18:39 | PPU BUKIT KETERI 1K5B | PPU BUKIT KETERI 1K5B | TMN SISWA KAN02609 - PDB PUSAT MATRIKULASI KAN00860 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 03-02-2024 18:50 | 03-02-2024 18:50 | 0 | 03-02-2024 21:25 | 13-02-2024 00:28 | 219 | 13-02-2024 00:54 | 222.25
Northern | K1 | TRIPPING-PLS-24-00009 | 2610/20240204/033 | Perlis | Perlis | 11kV | Underground | 04-02-2024 19:45 | PMU CHUPING CB3 | PDB UITM ARAU KAN00863 CB1 | PPU NAKA 6K5 - | Open Circuit | Soil Movement | Cable XLPE | CABLE | 04-02-2024 20:00 | 04-02-2024 20:10 | 10 | 06-02-2024 21:35 | 18-02-2024 23:17 | 289 | 18-02-2024 23:20 | 339.58
Northern | K1 | TRIPPING-KED-24-00078 | 0245/20240205/001 | Kedah | Kuala Nerang | 11kV | Overhead | 05-02-2024 07:56 | PPU NAKA 6K5 | PPU NAKA 6K5 |  | Insulation Breakdown | Insulation Deterioration | Cable Termination | NO FAULT | 05-02-2024 07:57 | 05-02-2024 08:30 | 33 |  |  |  | 05-02-2024 09:57 | 2.02
Northern | K1 | TRIPPING-PLS-24-00010 | 2610/20240206/020 | Perlis | Perlis | 11kV | Underground | 06-02-2024 03:10 | PPU SHORUBBER CB5 | BEHOR MENTALOON KAN00975 CB1 | HTL PUTRA BRASMANA K.PERLIS KAN01195 - PDB KOMP LKIM K.PERLIS KAN01194 | Insulation Breakdown | Insulation Deterioration | Transition Joint | TRANSIENT | 06-02-2024 03:20 | 06-02-2024 04:00 | 40 |  |  |  | 06-02-2024 05:52 | 2.7
Northern | K1 | TRIPPING-PLS-24-00011 | 2610/20240206/035 | Perlis | Perlis | 11kV | Underground | 06-02-2024 10:39 | PMU KUALA PERLIS CB6 | PDB TOP FOOD KAN01202 CB1 | PBT DRIVING RANGE KJT00212 - PDB TMN GOLF NO4 KJT00213 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 06-02-2024 10:53 | 06-02-2024 11:15 | 22 | 15-02-2024 10:38 | 15-02-2024 22:54 | 12 | 15-02-2024 23:15 | 228.6
Northern | K1 | TRIPPING-KED-24-00082 | 0242/20240206/040 | Kedah | Jitra | 11kV | Underground | 06-02-2024 16:18 | PPU DARULAMAN 8K5 | PPU DARULAMAN 8K5 |  | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 06-02-2024 16:32 | 06-02-2024 17:00 | 28 | 07-02-2024 22:43 | 08-02-2024 23:33 | 24 | 08-02-2024 23:37 | 55.32
Northern | K1 | TRIPPING-KED-24-00092 | 0242/20240210/033 | Kedah | Jitra | 11kV | Overhead | 10-02-2024 10:24 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00895 CB1 | TMN BUNGA PADI KAN00388 - PDB LPP BINTONG KAN00400 | Insulation Breakdown | Tree | Isolator Link | TRANSIENT | 10-02-2024 10:34 | 10-02-2024 10:55 | 21 |  |  |  | 10-02-2024 11:40 | 1.27
Northern | K1 | TRIPPING-PLS-24-00012 | 2610/20240212/026 | Perlis | Perlis | 11kV | Underground | 12-02-2024 02:55 | PMU KUALA PERLIS CB2 | TMN BUNGA PADI KAN00388 CB1 | PBT FELCRA KUBANG PALAS KKN00356 - PBT BUKIT ULAR KKN00354 | Open Circuit | Soil Movement | Straight Through Joint | CABLE | 12-02-2024 02:58 | 12-02-2024 03:41 | 43 | 13-02-2024 21:34 | 21-02-2024 22:33 | 192 | 21-02-2024 22:40 | 235.75
Northern | K1 | TRIPPING-KED-24-00100 | 0245/20240213/002 | Kedah | Kuala Nerang | 11kV | Underground | 13-02-2024 10:05 | PPU KUALA NERANG 8K5 | PPU KUALA NERANG 8K5 | PVCB RPA SANTAN 2 KAN02465 - PLB PADANG LATI KAN00771 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable PILC | CABLE | 13-02-2024 10:08 | 13-02-2024 10:28 | 20 | 13-02-2024 21:12 | 23-02-2024 04:20 | 223 | 23-02-2024 04:35 | 234.5
Northern | K1 | TRIPPING-PLS-24-00013 | 2610/20240214/015 | Perlis | Perlis | 11kV | Underground | 14-02-2024 03:12 | PMU KANGAR CB5 | PVCB REPOH CERIA-VVIP KAN02632 CB1 | PDB LOJI AIR SG. BARU - PDT RUMAH PAM SMPG EMPAT KAN01144 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 14-02-2024 03:29 | 14-02-2024 03:50 | 21 | 29-02-2024 10:58 | 29-02-2024 22:12 | 11 | 29-02-2024 22:19 | 379.12
Northern | K1 | TRIPPING-PLS-24-00014 | 2610/20240214/179 | Perlis | Perlis | 11kV | Underground | 14-02-2024 14:42 | PPU SIMPANG EMPAT CB9 | PPU SIMPANG EMPAT CB9 | PPU BUKIT KETERI 6K5B - PDB TMN BESERI JAYA KAN00177 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 14-02-2024 14:47 | 14-02-2024 15:28 | 41 | 16-02-2024 23:39 | 20-02-2024 22:08 | 94 | 20-02-2024 22:30 | 151.8
Northern | K1 | TRIPPING-PLS-24-00015 | 2610/20240216/029 | Perlis | Perlis | 11kV | Underground | 16-02-2024 20:36 | PPU BUKIT KETERI 6K5B | PPU BUKIT KETERI 6K5B | PAT LONG BOH TENGAH KAN02313 - PDT SK LONG BOH KAN01029 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 16-02-2024 20:39 | 16-02-2024 20:56 | 17 | 17-02-2024 21:36 | 27-02-2024 22:07 | 240 | 27-02-2024 22:18 | 265.7
Northern | K1 | TRIPPING-PLS-24-00016 | 2610/20240220/017 | Perlis | Perlis | 11kV | Underground | 20-02-2024 14:10 | PPU SHORUBBER CB3 | PDB MIEL KUKUM JEJAWI KAN00733 CB1 | CSU TANGKI AIR SIMPANG 4 KAN03194 - SEK MEN SANGLANG KAN01093 | Insulation Breakdown | Soil Movement | Straight Through Joint | OVERHEAD LINES | 20-02-2024 14:11 | 20-02-2024 14:45 | 34 | 20-02-2024 23:06, 28-02-2024 21:02 | 24-02-2024 09:18, 29-02-2024 09:53 | 82, 12 | 29-02-2024 10:10 | 212
Northern | K1 | TRIPPING-PLS-24-00017 | 2610/20240220/046 | Perlis | Perlis | 11kV | Underground | 20-02-2024 19:41 | PPU SIMPANG EMPAT CB5 | PPU SIMPANG EMPAT CB5 | PBT PIDA 8 KJT01349 - PBT PIDA 14 KJT01350 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 20-02-2024 19:46 | 20-02-2024 20:28 | 42 | 24-02-2024 09:25 | 24-02-2024 22:42 | 13 | 24-02-2024 22:34 | 98.88
Northern | K1 | TRIPPING-KED-24-00122 | 0242/20240222/024 | Kedah | Jitra | 11kV | Underground | 22-02-2024 12:04 | PPU MINI PPU KERPAN KRPN 3K5 | PPU MINI PPU KERPAN KRPN 3K5 | PAT PADANG PETANI KAN01050 - PDB KLG BERAS KUDUNG KAN01051 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 22-02-2024 12:06 | 22-02-2024 12:50 | 44 | 22-02-2024 20:36 | 24-02-2024 17:41 | 45 | 24-02-2024 18:25 | 54.35
Northern | K1 | TRIPPING-PLS-24-00018 | 2610/20240222/055 | Perlis | Perlis | 11kV | Underground | 22-02-2024 22:53 | PPU SIMPANG EMPAT CB4 | PPU SIMPANG EMPAT CB4 | KRC KKN00845 - PBT KG. PADANG NYIOR KKN00301 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 22-02-2024 22:53 | 22-02-2024 23:35 | 42 | 23-02-2024 22:10 | 25-02-2024 22:18 | 48 | 25-02-2024 22:27 | 71.57
Northern | K1 | TRIPPING-KED-24-00126 | 0245/20240224/002 | Kedah | Kuala Nerang | 11kV | Underground | 24-02-2024 10:37 | PPU KUALA NERANG 10K5 | PPU KUALA NERANG 10K5 | PADAT KLINIK KESIHATAN NAKA KKN00734 - PDB BDR BARU NAKA KKN00373 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 24-02-2024 10:38 | 24-02-2024 11:06 | 28 | 24-02-2024 18:51 | 27-02-2024 22:33 | 75 | 27-02-2024 23:30 | 84.88
Northern | K1 | TRIPPING-KED-24-00129 | 0245/20240225/014 | Kedah | Kuala Nerang | 11kV | Underground | 25-02-2024 12:56 | PPU NAKA 4K5 | PPU NAKA 4K5 | PDB KG BARU NAMI KSK00695 - PATOD KG. TANJUNG PIRING KKN00447, - PBT SMPG LUBOK MERBAU KSK00175 - PBT KUALA BERIS KSK00169 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 25-02-2024 13:00 | 25-02-2024 13:42 | 42 | 25-02-2024 21:39 | 05-03-2024 22:59 | 217 | 05-03-2024 23:35 | 226.65
Northern | K1 | TRIPPING-KED-24-00133 | 0245/20240226/041 | Kedah | Kuala Nerang | 11kV | Underground | 26-02-2024 22:24 | PPU NAKA 6K5 | PPU NAKA 6K5 | PPU SHORUBBER CB10 - PDB TMN SEMATANG JAYA KAN00985 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE, CABLE | 26-02-2024 22:45 | 26-02-2024 23:08 | 23 | 27-02-2024 18:39, 28-02-2024 09:16 | 28-02-2024 18:43, 01-03-2024 20:25 | 24, 59 | 02-03-2024 23:30 | 121.1
Northern | K1 | TRIPPING-PLS-24-00019 | 2610/20240226/211 | Perlis | Perlis | 11kV | Underground | 26-02-2024 23:25 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 | PLB BATAS BENGKOK KJT01417 - R/P MADA MTG KERENG KJT19385 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 26-02-2024 23:50 | 27-02-2024 00:00 | 10 | 27-02-2024 22:49 | 17-03-2024 22:55 | 456 | 17-03-2024 23:21 | 479.93
Northern | K1 | TRIPPING-KED-24-00138 | 0242/20240228/033 | Kedah | Jitra | 11kV | Underground | 28-02-2024 15:30 | PPU LOJI AIR ARAU GIS 11K5 | PDB KLG BERAS PERING KJT01776 CB1 | PDB RUMAH PAM KG. BKT SENA KKN00562 - PLB KG. TANJUNG LUAR KKN00142 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 28-02-2024 15:38 | 28-02-2024 16:05 | 27 | 28-02-2024 22:36 | 03-03-2024 19:35 | 92 | 03-03-2024 20:11 | 100.68
Northern | K1 | TRIPPING-KED-24-00149 | 0245/20240301/003 | Kedah | Kuala Nerang | 11kV | Underground | 01-03-2024 16:36 | PPU KUALA NERANG 2K5 | A/R SEK MEN PEDU | TIMAH TASOH POND 2 JPS KAN02945 - PDB VCB TIMAH TASOH KAN00170 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 01-03-2024 16:38 | 01-03-2024 17:16 | 38 | 02-03-2024 16:35 | 04-03-2024 21:01 | 52 | 04-03-2024 21:28 | 76.87
Northern | K1 | TRIPPING-PLS-24-00020 | 2610/20240302/036 | Perlis | Perlis | 11kV | Underground | 02-03-2024 19:13 | PPU PADANG BESAR CB9 | PBT S/S FRIM KAN00113 | PPU SHORUBBER CB5 - PBT KG. SIAM KAN02186 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 02-03-2024 19:32 | 02-03-2024 20:14 | 42 | 18-03-2024 08:28 | 18-03-2024 23:09 | 14 | 19-03-2024 00:28 | 389.25
Northern | K1 | TRIPPING-PLS-24-00021 | 2610/20240303/031 | Perlis | Perlis | 11kV | Underground | 03-03-2024 04:37 | PPU SHORUBBER CB5 | PPU SHORUBBER CB5 | PDB TMN KEMAJUAN 1 KAN00582 - PDB TMN KEMAJUAN 2 KAN00581 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE |  | 03-03-2024 05:17 | 0 | 03-03-2024 20:36, 07-03-2024 23:29 | 07-03-2024 23:22, 14-03-2024 23:07 | 98, 167 | 14-03-2024 23:31 | 282.9
Northern | K1 | TRIPPING-PLS-24-00022 | 2610/20240303/020 | Perlis | Perlis | 11kV | Underground | 03-03-2024 04:38 | PPU SHORUBBER CB4 | PVCB TMN JALI KAN02329 | PBT KG. DANGLAU KSK00184 - PLB KUBANG KESOM KSK00181 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE |  | 03-03-2024 05:30 | 0 | 04-03-2024 00:15, 20-03-2024 22:30 | 20-03-2024 22:07, 21-03-2024 12:43 | 405, 14 | 21-03-2024 14:09 | 441.52
Northern | K1 | TRIPPING-KED-24-00157 | 0245/20240304/016 | Kedah | Kuala Nerang | 11kV | Underground | 04-03-2024 17:43 | PPU NAKA 6K5 | PPU NAKA 6K5 | FISHING NET KAN00068 - PLB FELDA MATA AIR 2 KAN02273 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE |  | 04-03-2024 18:28 | 0 | 06-03-2024 09:32 | 06-03-2024 23:11 | 13 | 06-03-2024 23:40 | 53.95
Northern | K1 | TRIPPING-PLS-24-00023 | 2610/20240305/048 | Perlis | Perlis | 11kV | Underground | 05-03-2024 16:14 | PPU PADANG BESAR CB2 | FISHING NET KAN00068 | PDB RUMAH PAM GUAR SANJI - PDB TELEKOM GUAR SANJI KAN00953 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE |  | 05-03-2024 17:20 | 0 | 19-03-2024 11:28 | 20-03-2024 18:11 | 30 | 20-03-2024 19:05 | 362.85
Northern | K1 | TRIPPING-PLS-24-00024 | 2610/20240307/090 | Perlis | Perlis | 11kV | Overhead | 07-03-2024 19:40 | PPU LOJI AIR ARAU GIS 30 | PPU LOJI AIR ARAU GIS 30 | PAT KEPALA 20 BEHOR GELAM KAN00978 - PAT BEHOR GELAM KAN00979 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 07-03-2024 19:41 | 07-03-2024 19:51 | 10 | 08-03-2024 19:16 | 03-04-2024 12:12 | 616 | 03-04-2024 12:31 | 640.85
Northern | K1 | TRIPPING-PLS-24-00026 | 2610/20240316/023 | Perlis | Perlis | 11kV | Underground | 16-03-2024 03:07 | PPU SHORUBBER CB5 | PPU SHORUBBER CB5 | KOMPLEK PERNIAGAAN AMAN KJT19164 - PDB TMN JITRA JAYA KJT00437 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 16-03-2024 03:40 | 16-03-2024 04:09 | 29 | 21-03-2024 23:07 | 22-03-2024 12:06 | 12 | 22-03-2024 12:23 | 153.27
Northern | K1 | TRIPPING-KED-24-00181 | 0242/20240318/012 | Kedah | Jitra | 11kV | Underground | 18-03-2024 03:09 | PMU TANJUNG PAUH TP19 | PMU TANJUNG PAUH TP19 | S/S BATU 25 KJT00817 - S/S RMU BATU 26 KJT00818 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 18-03-2024 03:11 | 18-03-2024 03:28 | 17 | 18-03-2024 16:59, 29-03-2024 23:30 | 20-03-2024 01:28, 30-03-2024 23:05 | 32, 23 | 30-03-2024 23:15 | 308.1
Northern | K1 | TRIPPING-KED-24-00183 | 0242/20240318/076 | Kedah | Jitra | 11kV | Underground | 18-03-2024 10:08 | PMU BUKIT KAYU HITAM BKH4 | PMU BUKIT KAYU HITAM BKH4 | PDL KLG BERAS KERPAN KJT01457 - TMN KELISA AIR HITAM KJT19409 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 18-03-2024 10:15 | 18-03-2024 10:47 | 32 | 20-03-2024 01:23 | 20-03-2024 22:42 | 21 | 20-03-2024 23:00 | 60.87
Northern | K1 | TRIPPING-KED-24-00184 | 0242/20240318/148 | Kedah | Jitra | 11kV | Underground | 18-03-2024 17:24 | PPU MINI PPU KERPAN KRPN 5K5 | PPU MINI PPU KERPAN KRPN 5K5 |  | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE |  | 18-03-2024 18:13 | 0 | 19-03-2024 00:19 | 19-03-2024 22:54 | 22 | 20-03-2024 00:00 | 30.6
Northern | K1 | TRIPPING-KED-24-00191 | 0242/20240320/042 | Kedah | Jitra | 11kV | Overhead | 20-03-2024 17:40 | PPU JERLUN SJ4 | PPU JERLUN SJ14 | PENGKALAN MERIN KAN02071 - PDB PLAZA KUALA PERLIS KAN02068 | Insulation Breakdown | Insulation Deterioration | Conductor | NO FAULT |  | 20-03-2024 18:25 | 0 |  |  |  | 20-03-2024 18:50 | 1.17
Northern | K1 | TRIPPING-PLS-24-00027 | 2610/20240321/053 | Perlis | Perlis | 11kV | Overhead | 21-03-2024 16:33 | PMU KUALA PERLIS CB6 | PDB TOP FOOD KAN01202 | PDB SM SAINS POKOK SENA KAS02569 - PLB TMN PERTAMA KAS02572, - KG RAMBUTAN KKN00837 - PATOD KG. BAKONG KKN00068 | Flash over | Animal | Drop Out Fuse | CABLE | 21-03-2024 16:37 | 21-03-2024 17:20 | 43 | 22-03-2024 22:53 | 30-03-2024 22:46 | 191 | 30-03-2024 22:53 | 222.33
Northern | K1 | TRIPPING-KED-24-00195 | 0245/20240321/097 | Kedah | Kuala Nerang | 11kV | Underground | 21-03-2024 21:45 | PPU KUALA NERANG 6K5 | PPU KUALA NERANG 6K5 | TMN IDAMAN KJT18999 - S/SUIS INTRA GROWTH KJT18947 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE, CABLE | 21-03-2024 21:47 | 21-03-2024 22:25 | 38 | 22-03-2024 11:58, 22-03-2024 15:33, 27-03-2024 23:28 | 23-03-2024 10:08, 26-03-2024 02:50, 28-03-2024 04:25 | 22, 83, 4 | 28-03-2024 05:00 | 151.25
Northern | K1 | TRIPPING-KED-24-00198 | 0242/20240323/061 | Kedah | Jitra | 11kV | Underground | 23-03-2024 18:52 | PMU TANJUNG PAUH TP18 | PMU TANJUNG PAUH TP18 |  | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 23-03-2024 19:00 | 23-03-2024 19:41 | 41 | 24-03-2024 22:09 | 26-03-2024 22:48 | 48 | 26-03-2024 23:10 | 76.3
Northern | K1 | TRIPPING-KED-24-00199 | 0240/20240323/077 | Kedah | Jitra | 11kV | Underground | 23-03-2024 18:57 | PPU PELUBANG PL3 | PDB SK PENGHULU HJ DARUS KJT00694 | PDB TMN SRI SANGLANG KJT01586 - | Insulation Breakdown | Insulation Deterioration | Cable XLPE | NO FAULT | 23-03-2024 19:00 | 23-03-2024 20:32 | 92 |  |  |  | 23-03-2024 21:31 | 2.57
Northern | K1 | TRIPPING-KED-24-00200 | 0242/20240324/010 | Kedah | Jitra | 11kV | Substation | 24-03-2024 01:55 | PPU MINI PPU KERPAN KRPN 5K5 | PPU MINI PPU KERPAN KRPN 5K5 | PPU PADANG BESAR CB9 - PVCB TITI TINGGI KAN00090 | Dielectric | Dielectric Deterioration | RMU SF6 | SWITCHGEAR | 24-03-2024 02:01 | 24-03-2024 02:45 | 44 | 30-03-2024 11:46 | 31-03-2024 01:13 | 13 | 31-03-2024 01:40 | 167.75
Northern | K1 | TRIPPING-PLS-24-00028 | 2610/20240324/004 | Perlis | Perlis | 11kV | Underground | 24-03-2024 07:08 | PPU PADANG BESAR CB9 | PPU PADANG BESAR CB9 |  | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 24-03-2024 07:21 | 24-03-2024 07:36 | 15 | 25-03-2024 21:28 | 25-03-2024 23:15 | 1 | 26-03-2024 22:33 | 63.42
Northern | K1 | TRIPPING-PLS-24-00029 | 2610/20240325/034 | Perlis | Perlis | 11kV | Substation | 25-03-2024 07:00 | PPU BUKIT KETERI 6K5B | PDB TMN BESERI JAYA KAN00176 | PPU KUALA NERANG 4K5 - PDB TELEKOM KUALA NERANG KKN00001 | Dielectric | Dielectric Deterioration | RMU SF6 | NO FAULT |  | 25-03-2024 07:39 | 0 |  |  |  | 25-03-2024 07:44 | 0.73
Northern | K1 | TRIPPING-KED-24-00206 | 0245/20240325/011 | Kedah | Kuala Nerang | 11kV | Underground | 25-03-2024 18:22 | PPU KUALA NERANG 4K5 | PPU KUALA NERANG 4K5 | PDB TELEKOM CHANGLUN KJT00893 - SEK MEN CHANGLUN KJT00892 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 25-03-2024 18:27 | 25-03-2024 18:48 | 21 | 26-03-2024 15:38 | 27-03-2024 05:23 | 13 | 27-03-2024 05:50 | 35.47
Northern | K1 | TRIPPING-KED-24-00207 | 0242/20240325/074 | Kedah | Jitra | 11kV | Underground | 25-03-2024 23:46 | PPU CHANGLOON CL6 | PPU CHANGLOON CL6 |  | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE |  | 26-03-2024 00:12 | 0 | 26-03-2024 23:17 | 29-03-2024 22:16 | 70 | 29-03-2024 22:30 | 94.73
Northern | K1 | TRIPPING-PLS-24-00030 | 2610/20240326/015 | Perlis | Perlis | 11kV | Substation | 26-03-2024 04:26 | PPU SIMPANG EMPAT CB4 | PPU SIMPANG EMPAT CB4 | PLB TITI TINGGI ULU KAN00102 - PBT BUKIT CABANG KAN02102 | Dielectric | Dielectric Deterioration | RMU SF6 | NO FAULT |  | 26-03-2024 05:15 | 0 |  |  |  | 26-03-2024 05:37 | 1.18
Northern | K1 | TRIPPING-PLS-24-00031 | 2610/20240326/099 | Perlis | Perlis | 11kV | Underground | 26-03-2024 22:54 | PPU PADANG BESAR CB9 | PVCB TITI TINGGI KAN00091 | STN SUIS POLITEKNIK - PDB POLITEKNIK 1 KJT00147 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 26-03-2024 22:56 | 26-03-2024 23:15 | 19 | 04-04-2024 12:04 | 04-04-2024 23:43 | 11 | 04-04-2024 23:56 | 217.03
Northern | K1 | TRIPPING-KED-24-00212 | 0242/20240328/005 | Kedah | Jitra | 11kV | Underground | 28-03-2024 01:25 | PMU TANJUNG PAUH TP16 | PMU TANJUNG PAUH TP16 | PPU DARULAMAN 10K5 - PDB TMN GEMILANG (JIT) | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 28-03-2024 01:27 | 28-03-2024 02:00 | 33 | 01-04-2024 21:55 | 02-04-2024 11:06 | 13 | 02-04-2024 11:15 | 129.83
Northern | K1 | TRIPPING-KED-24-00216 | 0242/20240329/180 | Kedah | Jitra | 11kV | Underground | 29-03-2024 00:06 | PPU DARULAMAN 10K5 | PPU DARULAMAN 10K5 | S/S RMU BATU 26 KJT00818 - S/S BATU 25 KJT00817 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 29-03-2024 00:11 | 29-03-2024 00:16 | 5 | 29-03-2024 22:36 | 01-04-2024 07:22 | 56 | 01-04-2024 09:40 | 81.57
Northern | K1 | TRIPPING-KED-24-00244 | 0242/20240407/049 | Kedah | Jitra | 11kV | Underground | 07-04-2024 07:03 | PMU BUKIT KAYU HITAM BKH4 | PDB PROTAB AGROBASE KJT01138 |  | Insulation Breakdown | Insulation Deterioration | Transition Joint | CABLE | 07-04-2024 07:06 | 07-04-2024 07:50 | 44 | 08-04-2024 09:50 | 15-04-2024 08:12 | 166 | 15-04-2024 10:29 | 195.43
Northern | K1 | TRIPPING-KED-24-00251 | 0242/20240408/080 | Kedah | Jitra | 11kV | Overhead | 08-04-2024 17:02 | PMU BUKIT KAYU HITAM BKH8 | STN SUIS ICQS KJT19258 | INSTITUT AMINUDIN BAKI KJT1583 - PDB PLAZA TOL JITRA KJT00207 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | TRANSIENT | 08-04-2024 18:00 | 08-04-2024 18:40 | 40 |  |  |  | 08-04-2024 19:51 | 2.82
Northern | K1 | TRIPPING-KED-24-00260 | 0242/20240414/002 | Kedah | Jitra | 11kV | Underground | 14-04-2024 00:10 | PPU DARULAMAN 8K5 | PPU DARULAMAN 8K5 | PMU TANJUNG PAUH TP20 - PLB TMN KENANGA-JITRA KJT00001 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 14-04-2024 00:16 | 14-04-2024 00:30 | 14 | 14-04-2024 23:01, 17-04-2024 09:17 | 15-04-2024 03:58, 17-04-2024 21:13 | 4, 11 | 17-04-2024 22:55 | 94.75
Northern | K1 | TRIPPING-KED-24-00265 | 0242/20240415/197 | Kedah | Jitra | 11kV | Underground | 15-04-2024 23:03 | PMU TANJUNG PAUH TP20 | PMU TANJUNG PAUH TP20 | PPU PELUBANG PL1 - LOJI AIR PELUBANG KJT00680 | Insulation Breakdown | Insulation Deterioration | Transition Joint | CABLE | 15-04-2024 23:05 | 15-04-2024 23:11 | 6 | 16-04-2024 20:33 | 20-04-2024 20:13 | 95 | 20-04-2024 22:30 | 119.45
Northern | K1 | TRIPPING-KED-24-00277 | 0242/20240421/029 | Kedah | Jitra | 11kV | Underground | 21-04-2024 17:10 | PPU PELUBANG PL1 | PPU PELUBANG PL1 | TMN UTARA JAYA K.PERLIS-VVIP KAN01197 - PAT PADANG BESAR SELATAN KAN01208 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 21-04-2024 17:12 | 21-04-2024 17:52 | 40 | 21-04-2024 20:04 | 22-04-2024 04:24 | 8 | 22-04-2024 05:09 | 11.98
Northern | K1 | TRIPPING-PLS-24-00034 | 2610/20240421/075 | Perlis | Perlis | 11kV | Underground | 21-04-2024 20:07 | PMU KUALA PERLIS CB11 | PDB KUALA PERLIS KAN01164 | PLB PDG SERA KJT01284 - | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 21-04-2024 20:10 | 21-04-2024 20:45 | 35 | 23-04-2024 10:44 | 23-04-2024 22:42 | 11 | 23-04-2024 22:55 | 50.8
Northern | K1 | TRIPPING-KED-24-00280 | 0242/20240423/032 | Kedah | Jitra | 11kV | Overhead | 23-04-2024 02:40 | PPU KODIANG KD5 | PPU KODIANG KD5 | PDB KOMP KASTAM & IMIGRESEN KAN00023 - | Insulation Breakdown | Insulation Deterioration | Cable Termination | TRANSIENT | 23-04-2024 02:44 | 23-04-2024 03:15 | 31 |  |  |  | 23-04-2024 04:25 | 1.75
Northern | K1 | TRIPPING-PLS-24-00036 | 2610/20240425/052 | Perlis | Perlis | 11kV | Overhead | 25-04-2024 15:37 | PPU PADANG BESAR CB7 | PDB KOMP KASTAM & IMIGRESEN KAN00023 | SSD NO.1 KJT01142 - PAT BATU 26 KJT19463, - S/S BATU 25 KJT00815 - PLB INTER CHANGE KJT00814 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | NO FAULT | 25-04-2024 15:56 | 25-04-2024 16:20 | 24 |  |  |  | 25-04-2024 17:15 | 1.63
Northern | K1 | TRIPPING-KED-24-00297 | 0242/20240427/164 | Kedah | Jitra | 11kV | Underground | 27-04-2024 21:57 | PMU BUKIT KAYU HITAM BKH4 | PDB PROTAB AGROBASE KJT01138 | PAT SS BANGSAL LEBAH KAN00622 - | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE, CABLE | 27-04-2024 22:04 | 27-04-2024 22:25 | 21 | 28-04-2024 22:23, 28-04-2024 22:26 | 01-05-2024 00:52, 01-05-2024 00:55 | 50, 50 | 01-05-2024 02:10 | 76.22
Northern | K1 | TRIPPING-PLS-24-00037 | 2610/20240505/112 | Perlis | Perlis | 11kV | Overhead | 05-05-2024 23:32 | PMU KUALA PERLIS CB1 | PDB AMAN FISHMEAL KAN00623 | PDB LOJI AIR SG. BARU KAN01143 - PDT RUMAH PAM SMPG EMPAT KAN01144 | Insulation Breakdown | Animal | Isolator Link | NO FAULT | 05-05-2024 11:34 | 05-05-2024 11:59 | 25 |  |  |  | 06-05-2024 00:18 | 0.77
Northern | K1 | TRIPPING-PLS-24-00038 | 2610/20240506/035 | Perlis | Perlis | 11kV | Underground | 06-05-2024 06:09 | PMU KUALA PERLIS CB3 | PMU KUALA PERLIS CB3 | PLB BANK PERTANIAN - TMN KAYANG PERMAI KAN03092 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 06-05-2024 06:40 | 06-05-2024 07:08 | 28 | 09-05-2024 10:41 | 12-05-2024 21:54 | 83 | 12-05-2024 22:15 | 160.1
Northern | K1 | TRIPPING-PLS-24-00039 | 2610/20240507/021 | Perlis | Perlis | 11kV | Overhead | 07-05-2024 12:10 | PPU SIMPANG EMPAT CB6 | PPU SIMPANG EMPAT CB6 | PBT SG. BEREMBANG KAN01206 - PDB WATER TREATMENT KAN01205 | Insulation Breakdown | Animal | Isolator Link | NO FAULT | 07-05-2024 12:16 | 07-05-2024 12:38 | 22 | 07-05-2024 13:03 | 07-05-2024 13:18 | 0 | 07-05-2024 13:22 | 1.2
Northern | K1 | TRIPPING-PLS-24-00040 | 2610/20240508/025 | Perlis | Perlis | 11kV | Underground | 08-05-2024 04:28 | PMU KUALA PERLIS CB3 | PMU KUALA PERLIS CB3 |  | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 08-05-2024 04:40 | 08-05-2024 05:15 | 35 | 12-05-2024 10:08 | 12-05-2024 23:19 | 13 | 12-05-2024 23:32 | 115.07
Northern | K1 | TRIPPING-PLS-24-00041 | 2610/20240511/007 | Perlis | Perlis | 11kV | Overhead | 11-05-2024 08:10 | PPU PADANG BESAR CB12 | RPA PADANG BESAR KAN02911 | PAT PADANG BENTA KAN01223 - PBT SG. BARU SMPG EMPAT KAN01225 | Insulation Breakdown | Animal | Isolator Link | NO FAULT | 11-05-2024 10:15 | 11-05-2024 10:40 | 25 |  |  |  | 11-05-2024 11:04 | 2.9
Northern | K1 | TRIPPING-PLS-24-00042 | 2610/20240520/038 | Perlis | Perlis | 11kV | Overhead | 20-05-2024 10:45 | PPU SIMPANG EMPAT CB9 | PPU SIMPANG EMPAT CB9 | PATOD KG BARU SINTOK 2 KJT01836 - PDB TMN SEMARAK API KJT01835 | Open Circuit | Improper Installation | Straight Through Joint | CABLE | 20-05-2024 10:47 | 20-05-2024 11:10 | 23 | 20-05-2024 20:25, 22-05-2024 11:38 | 22-05-2024 09:49, 22-05-2024 16:57 | 37, 5 | 22-05-2024 17:34 | 54.82
Northern | K1 | TRIPPING-KED-24-00349 | 0242/20240521/022 | Kedah | Jitra | 11kV | Overhead | 21-05-2024 04:01 | PPU CHANGLOON CL5 | PPU CHANGLOON CL5 | PBT KG. TELOK KAN02462 - PBT KG. PELADANG KAN02461 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | OVERHEAD LINES | 21-05-2024 04:03 | 21-05-2024 05:00 | 57 | 21-05-2024 23:19 | 23-05-2024 21:35 | 46 | 23-05-2024 21:49 | 65.8
Northern | K1 | TRIPPING-PLS-24-00043 | 2610/20240521/022 | Perlis | Perlis | 11kV | Overhead | 21-05-2024 04:09 | PMU KUALA PERLIS CB5 | PMU KUALA PERLIS CB5 | PEKAN KAKI BUKIT KAN00139 - | Insulation Breakdown | Insulation Deterioration | Cable Termination | CABLE | 21-05-2024 04:15 | 21-05-2024 04:50 | 35 | 21-05-2024 20:35 | 25-05-2024 18:42 | 94 | 25-05-2024 19:05 | 110.93
Northern | K1 | TRIPPING-PLS-24-00044 | 2610/20240523/052 | Perlis | Perlis | 11kV | Overhead | 23-05-2024 15:20 | PPU PADANG BESAR CB2 | PEKAN KAKI BUKIT KAN00139 | PDB LKIM PADANG BESAR - PDB EMAS KERANJANG KAN00028 | Insulation Breakdown | Tree | Conductor | NO FAULT | 23-05-2024 15:25 | 23-05-2024 16:07 | 42 |  |  |  | 23-05-2024 17:16 | 1.93
Northern | K1 | TRIPPING-PLS-24-00045 | 2610/20240529/017 | Perlis | Perlis | 11kV | Overhead | 29-05-2024 09:58 | PPU PADANG BESAR CB7 | PDB KOMP KASTAM & IMIGRESEN KAN00023 | PBT KG. TANJUNG-ALS KKN00298 - PBT PADANG CENDERAI KKN00309 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 29-05-2024 10:04 | 29-05-2024 10:54 | 50 | 01-06-2024 09:33 | 01-06-2024 16:30 | 6 | 01-06-2024 16:50 | 78.87
Northern | K1 | TRIPPING-KED-24-00358 | 0245/20240529/027 | Kedah | Kuala Nerang | 11kV | Underground | 29-05-2024 16:04 | PPU KUALA NERANG 8K5 | PPU KUALA NERANG 8K5 | PLB BUNGA EMAS -RB17 KAN01079 - KEPALA BATAS PAUH KAN01080 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE |  | 29-05-2024 16:45 | 0 | 30-05-2024 18:13 | 01-06-2024 21:52 | 51 | 01-06-2024 23:11 | 79.12
Northern | K1 | TRIPPING-PLS-24-00046 | 2610/20240603/043 | Perlis | Perlis | 11kV | Underground | 03-06-2024 06:44 | PPU SIMPANG EMPAT CB4 | PPU SIMPANG EMPAT CB4 | PDB TMN SINGGAHSANA KAN00057 - PDB KOMP UPP PADANG BESAR KAN02090 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE |  | 03-06-2024 07:35 | 0 | 04-06-2024 20:25 | 09-06-2024 22:06 | 121 | 09-06-2024 22:35 | 159.85
Northern | K1 | TRIPPING-PLS-24-00047 | 2610/20240605/050 | Perlis | Perlis | 11kV | Underground | 05-06-2024 15:16 | PPU PADANG BESAR CB11 | PPU PADANG BESAR CB11 | CSU SOLAR KBJ HECMY KAN03139 - PLB KG.PERAWAH KAN00778 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 05-06-2024 15:18 | 05-06-2024 16:01 | 43 | 05-06-2024 20:20 | 11-06-2024 20:20 | 144 | 11-06-2024 21:00 | 149.73
Northern | K1 | TRIPPING-PLS-24-00048 | 2610/20240607/001 | Perlis | Perlis | 11kV | Overhead | 07-06-2024 07:06 | PMU CHUPING CB1 | PLB KAJI CUACA KAN00789 | PAT KUBANG JULOK 2 KKN00371 - | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 07-06-2024 07:30 | 07-06-2024 08:00 | 30 | 08-06-2024 11:32 | 08-06-2024 20:25 | 8 | 08-06-2024 20:36 | 37.5
Northern | K1 | TRIPPING-KED-24-00396 | 0245/20240612/006 | Kedah | Kuala Nerang | 11kV | Substation | 12-06-2024 08:53 | PPU NAKA 4K5 | PPU NAKA 4K5 | PATOD R/PAM MADA MEGAT DEWA KJT18985 - PLB LPN LANA BULU KJT01312 | Possible Animal | NA | Transient | TRANSIENT | 12-06-2024 08:55 | 12-06-2024 09:18 | 23 |  |  |  | 12-06-2024 11:00 | 2.12
Northern | K1 | TRIPPING-KED-24-00397 | 0242/20240612/140 | Kedah | Jitra | 11kV | Underground | 12-06-2024 21:06 | PPU LOJI AIR ARAU GIS 12K5 | PPU LOJI AIR ARAU GIS 12K5 | PLB CERGAS UTARA KJT01201 - | Insulation Breakdown | Soil Movement | Straight Through Joint | CABLE | 12-06-2024 21:13 | 12-06-2024 21:50 | 37 | 12-06-2024 23:44, 13-06-2024 20:58 | 12-06-2024 23:55, 15-06-2024 18:18 | 0, 45 | 15-06-2024 18:51 | 69.75
Northern | K1 | TRIPPING-KED-24-00398 | 0242/20240613/011 | Kedah | Jitra | 11kV | Substation | 13-06-2024 00:16 | PPU KODIANG KD1 | SSBT RUMAH PAM PERING KJT01634 | PAT KUBANG BADAK KAN00352 - | Dielectric | Dielectric Deterioration | RMU SF6 | SWITCHGEAR | 13-06-2024 00:33 | 13-06-2024 00:52 | 19 | 19-06-2024 08:52 | 20-06-2024 17:47 | 32 | 20-06-2024 19:30 | 187.23
Northern | K1 | TRIPPING-PLS-24-00049 | 2610/20240615/051 | Perlis | Perlis | 11kV | Substation | 15-06-2024 10:31 | PPU BUKIT KETERI 6K5B | PDB TMN BESERI JAYA KAN00176 | PLB TANJUNG SEBERANG KKN00287 - PBT KG. TG SEBERANG KKN00327 | Dielectric breakdown | Shorted By Animal | HV Cable (Tx Tail) | OVERHEAD LINES | 15-06-2024 10:31 | 15-06-2024 11:12 | 41 | 15-06-2024 11:47 | 15-06-2024 12:23 | 0 | 15-06-2024 12:45 | 2.23
Northern | K1 | TRIPPING-KED-24-00409 | 0245/20240616/015 | Kedah | Kuala Nerang | 11kV | Underground | 16-06-2024 12:25 | PPU KUALA NERANG 1K5 | PPU KUALA NERANG 1K5 | PDB SK PDG PERAHU-VVIP KJT00106 - PDB KG. KETUL-KETUL (NOP) KJT00105 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 16-06-2024 12:27 | 16-06-2024 13:01 | 34 | 16-06-2024 22:04 | 19-06-2024 20:45 | 70 | 19-06-2024 21:52 | 81.45
Northern | K1 | TRIPPING-KED-24-00423 | 0242/20240622/035 | Kedah | Jitra | 11kV | Overhead | 22-06-2024 09:54 | PPU LOJI AIR ARAU GIS 12K5 | PPU LOJI AIR ARAU GIS 12K5 | S/S BATU 25 KJT00815 - PLB INTER CHANGE KJT00814 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 22-06-2024 09:55 | 22-06-2024 11:20 | 85 | 22-06-2024 23:38, 23-06-2024 16:27 | 23-06-2024 02:40, 24-06-2024 21:10 | 3, 28 | 24-06-2024 21:35 | 59.68
Northern | K1 | TRIPPING-KED-24-00429 | 0242/20240624/126 | Kedah | Jitra | 11kV | Underground | 24-06-2024 16:59 | PMU BUKIT KAYU HITAM BKH4 | PDB PROTAB AGROBASE KJT01138 | PDB LOJI PENAPIS AIR KJT19342 - PBT KBG BETONG KJT00736 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 24-06-2024 17:06 | 24-06-2024 17:45 | 39 | 25-06-2024 22:44 | 28-06-2024 01:42 | 50 | 28-06-2024 03:35 | 82.6
Northern | K1 | TRIPPING-KED-24-00433 | 0242/20240625/024 | Kedah | Jitra | 11kV | Overhead | 25-06-2024 14:40 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01798 | SSD NO.1 KJT00824 - PAT BATU 26 KJT19463 | Insulation Breakdown | Insulation Deterioration | Conductor | CABLE | 25-06-2024 14:43 | 25-06-2024 15:26 | 43 | 26-06-2024 00:38 | 26-06-2024 22:10 | 21 | 26-06-2024 22:50 | 32.17
Northern | K1 | TRIPPING-KED-24-00435 | 0242/20240626/009 | Kedah | Jitra | 11kV | Underground | 26-06-2024 09:00 | PMU BUKIT KAYU HITAM BKH4 | PMU BUKIT KAYU HITAM BKH4 | PMU KUALA PERLIS CB13 - RE(RSO) AMBANG FIESTA 1 B1 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 26-06-2024 09:05 | 26-06-2024 09:38 | 33 | 27-06-2024 01:13 | 28-06-2024 01:45 | 24 | 28-06-2024 03:33 | 42.55
Northern | K1 | TRIPPING-PLS-24-00052 | RE/2610/20240626/PLS/00052 | Perlis | Perlis | 11kV | Underground | 26-06-2024 15:58 | PMU KUALA PERLIS CB13 | PMU KUALA PERLIS CB13 | PDB KLG ACL JATI KJT01804 - PDB TMN BAYAN MAS NO 3 KJT01817 |  |  |  | CABLE | 26-06-2024 16:00 | 26-06-2024 16:15 | 15 |  |  |  | 26-06-2024 22:20 | 6.37
Northern | K1 | TRIPPING-KED-24-00439 | 0242/20240701/023 | Kedah | Jitra | 11kV | Underground | 01-07-2024 00:54 | PMU BUKIT KAYU HITAM BKH5 | PMU BUKIT KAYU HITAM BKH5 |  | Open Circuit | Soil Movement | Cable XLPE | CABLE | 01-07-2024 00:57 | 01-07-2024 01:15 | 18 | 01-07-2024 22:33 | 03-07-2024 02:11 | 27 | 03-07-2024 02:30 | 49.6
Northern | K1 | TRIPPING-KED-24-00441 | 0245/20240701/002 | Kedah | Kuala Nerang | 11kV | Underground | 01-07-2024 08:20 | PPU NAKA 4K5 | PPU NAKA 4K5 | PLB KRAFTANGAN - PDB TMN BUMITA KAN00596 | Possible Animal | NA | Transient | TRANSIENT | 01-07-2024 08:26 | 01-07-2024 08:57 | 31 |  |  |  | 01-07-2024 09:40 | 1.33
Northern | K1 | TRIPPING-PLS-24-00053 | 2610/20240701/066 | Perlis | Perlis | 11kV | Underground | 01-07-2024 23:42 | PMU KUALA PERLIS CB8 | PMU KUALA PERLIS CB8 | PPU UNIMAP GIS 2K5 - FELDA CHUPING NO.2 KAN02680 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 01-07-2024 23:50 |  | 0 | 02-07-2024 21:44 | 04-07-2024 22:15 | 48 | 04-07-2024 22:42 | 71
Northern | K1 | TRIPPING-PLS-24-00054 | 2610/20240702/007 | Perlis | Perlis | 11kV | Substation | 02-07-2024 04:42 | PPU UNIMAP GIS 2K5 | PPU UNIMAP GIS 2K5 |  | Dielectric | Vermin Encroachment | Circuit Breaker | CABLE | 02-07-2024 05:00 | 02-07-2024 05:18 | 18 | 07-07-2024 10:52 | 07-07-2024 21:45 | 10 | 07-07-2024 22:05 | 137.38
Northern | K1 | TRIPPING-PLS-24-00055 | 2610/20240704/034 | Perlis | Perlis | 11kV | Substation | 04-07-2024 11:49 | PPU SHORUBBER CB5 | BEHOR MENTALOON KAN00975 | PAT MADA KURUNG ANAI KAN00949 - PBT MADA GUAR SANJI KAN00948 | Dielectric breakdown | Insufficient Clearance | HV Cable (Tx Tail) | TRANSIENT | 04-07-2024 11:57 | 04-07-2024 12:30 | 33 |  |  |  | 04-07-2024 13:04 | 1.25
Northern | K1 | TRIPPING-PLS-24-00056 | 2610/20240708/049 | Perlis | Perlis | 11kV | Underground | 08-07-2024 10:49 | PPU LOJI AIR ARAU GIS 5K5 | PPU LOJI AIR ARAU GIS 5K5 | PDB TMN TG SARINA 4 KJT00650 - PDB TMN TG SARINA 1 KJT00649 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 08-07-2024 10:52 | 08-07-2024 11:34 | 42 | 09-07-2024 00:50, 11-07-2024 10:03 | 11-07-2024 10:00, 11-07-2024 21:44 | 57, 11 | 11-07-2024 21:55 | 83.1
Northern | K1 | TRIPPING-KED-24-00465 | 0242/20240709/014 | Kedah | Jitra | 11kV | Underground | 09-07-2024 03:49 | PPU DARULAMAN 8K5 | TMN TUNKU SARINA NO 6 KJT19072 | PDB TMN PULASAN F1 KJT00228 - TMN BELIMBING FASA 1 KJT18978 | Open Circuit | Improper Installation | Cable XLPE | CABLE | 09-07-2024 03:51 | 09-07-2024 04:22 | 31 | 09-07-2024 17:50 | 12-07-2024 10:16 | 64 | 12-07-2024 10:35 | 78.77
Northern | K1 | TRIPPING-KED-24-00477 | 0242/20240714/005 | Kedah | Jitra | 11kV | Underground | 14-07-2024 07:22 | PPU DARULAMAN 3K5 | PPU DARULAMAN 3K5 | PAT ULU PAUH KAN00884 - PBT PADANG CEMPA KAN00883 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 14-07-2024 07:26 | 14-07-2024 07:40 | 14 | 14-07-2024 22:16 | 05-08-2024 09:11 | 514 | 05-08-2024 12:07 | 532.75
Northern | K1 | TRIPPING-PLS-24-00058 | 2610/20240716/129 | Perlis | Perlis | 11kV | Underground | 16-07-2024 19:25 | PPU POLITEKNIK PAUH PERLIS 3 | PPU POLITEKNIK PAUH PERLIS 3 | PDB RPA TAMBUN TULANG KAN01000 - | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 16-07-2024 19:32 | 16-07-2024 19:57 | 25 | 17-07-2024 20:43 | 05-09-2024 22:10 | 1201 | 05-09-2024 22:31 | 1227.1
Northern | K1 | TRIPPING-PLS-24-00059 | 2610/20240717/091 | Perlis | Perlis | 11kV | Substation | 17-07-2024 12:23 | PPU SHORUBBER CB5 | BEHOR MENTALOON KAN00975 | PBT BATU 25 KJT00871 - PDT SEMARAK API NO.3 KJT19402 | Dielectric breakdown | Insufficient Clearance | HV Cable (Tx Tail) | NO FAULT | 17-07-2024 12:30 | 17-07-2024 13:00 | 30 |  |  |  | 17-07-2024 13:18 | 0.92
Northern | K1 | TRIPPING-KED-24-00490 | 0242/20240718/014 | Kedah | Jitra | 11kV | Underground | 18-07-2024 09:51 | PMU BUKIT KAYU HITAM BKH8 | PLB SMPG BKT.TANGGA KJT00877 | PATOD FELCRA KUBANG KENYENG KKN00756 - KEDA KBG KENYENG 2 KKN00818 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 18-07-2024 10:43 | 18-07-2024 11:20 | 37 |  |  |  | 20-07-2024 22:19 | 60.47
Northern | K1 | TRIPPING-KED-24-00493 | 0245/20240719/001 | Kedah | Kuala Nerang | 11kV | Underground | 19-07-2024 09:54 | PPU NAKA 3K5 | PPU NAKA 3K5 | PLB ALAT SUIS TEMPATAN KAN01177 - PDB 3 UNIT KLG KAN01178 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 19-07-2024 09:56 | 19-07-2024 10:38 | 42 | 19-07-2024 22:44 | 25-07-2024 02:12 | 123 | 25-07-2024 03:18 | 137.4
Northern | K1 | TRIPPING-PLS-24-00060 | 2610/20240720/101 | Perlis | Perlis | 11kV | Underground | 20-07-2024 21:23 | PMU KUALA PERLIS CB11 | PMU KUALA PERLIS CB11 | PDB TMN DESA DARULAMAN KJT00578 - TMN DESA TANJUNG-ALS KJT19016 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 20-07-2024 21:34 | 20-07-2024 22:10 | 36 | 21-07-2024 22:36 | 27-07-2024 22:23 | 143 | 27-07-2024 22:40 | 169.28
Northern | K1 | TRIPPING-KED-24-00501 | 0242/20240723/075 | Kedah | Jitra | 11kV | Underground | 23-07-2024 23:35 | PMU TANJUNG PAUH TP9 | KOMERSIAL SQUARE KOLEJ HEIGHT KJT19376 | PDB TMN AMAN 2 KAN00794 - PDB TMN AMAN-VVIP KAN00392 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 23-07-2024 23:47 | 24-07-2024 00:20 | 33 | 24-07-2024 23:17 | 25-07-2024 17:55 | 18 | 25-07-2024 18:06 | 42.52
Northern | K1 | TRIPPING-PLS-24-00062 | 2610/20240725/017 | Perlis | Perlis | 11kV | Underground | 25-07-2024 16:43 | PMU KUALA PERLIS CB2 | TMN BUNGA PADI KAN00389 |  | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE |  | 25-07-2024 17:23 | 0 | 26-07-2024 21:02 | 07-08-2024 22:02 | 288 | 07-08-2024 22:38 | 317.92
Northern | K1 | TRIPPING-KED-24-00510 | 0242/20240727/018 | Kedah | Jitra | 11kV | Substation | 27-07-2024 14:48 | PMU TANJUNG PAUH TP8 | PMU TANJUNG PAUH TP8 | PDB KLG BAJA MK HOSBA KJT01692 - PDT YUNG HENG POULTRY KJT19442 | Thermal Failure | Contact Resistance | Circuit Breaker | SWITCHGEAR | 27-07-2024 15:30 |  | 0 | 27-07-2024 16:57, 05-08-2024 15:06 | 27-07-2024 17:35, 28-08-2024 17:49 | 0, 554 | 28-08-2024 17:53 | 771.08
Northern | K1 | TRIPPING-KED-24-00520 | 0242/20240802/003 | Kedah | Jitra | 11kV | Overhead | 02-08-2024 05:31 | PPU KODIANG KD1 | SSBT RUMAH PAM PERING KJT01149 | PUTRA HEIGHT 3 KAN02730 - PAT KOK KELANG 1-VVIP KAN00253 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 02-08-2024 05:37 | 02-08-2024 06:17 | 40 | 02-08-2024 21:27 | 05-08-2024 22:46 | 73 | 06-08-2024 00:07 | 90.6
Northern | K1 | TRIPPING-PLS-24-00065 | 2610/20240802/015 | Perlis | Perlis | 11kV | Underground | 02-08-2024 15:56 | PMU CHUPING CB6 | PMU CHUPING CB6 |  | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 02-08-2024 15:59 | 02-08-2024 16:25 | 26 | 08-08-2024 10:58 | 08-08-2024 23:07 | 12 | 09-08-2024 00:22 | 152.43
Northern | K1 | TRIPPING-PLS-24-00066 | 2610/20240803/010 | Perlis | Perlis | 11kV | Substation | 03-08-2024 07:04 | PMU KUALA PERLIS CB1 | PDB AMAN FISHMEAL KAN00623 | PDB PERUMAHAN LDG SG TEKAI KKN00642 - PBT KG. PADANG-K.NERANG KKN00435 | Dielectric breakdown | Shorted By Animal | HV Cable (Tx Tail) | TRANSIENT | 03-08-2024 07:04 | 03-08-2024 07:35 | 31 |  |  |  | 03-08-2024 08:26 | 1.37
Northern | K1 | TRIPPING-KED-24-00525 | 0245/20240804/011 | Kedah | Kuala Nerang | 11kV | Underground | 04-08-2024 15:37 | PPU NAKA 6K5 | PPU NAKA 6K5 | PAT PADANG MAJAI KAN00358 - PADAT MASJID AR-RAHMAN KAN03072 | Insulation Breakdown | Insulation Deterioration | Cable Termination | CABLE | 04-08-2024 15:44 | 04-08-2024 16:05 | 21 | 04-08-2024 23:08 | 06-08-2024 20:40 | 45 | 06-08-2024 21:28 | 53.85
Northern | K1 | TRIPPING-PLS-24-00067 | 2610/20240805/032 | Perlis | Perlis | 11kV | Overhead | 05-08-2024 00:01 | PPU BUKIT KETERI 6K5 | PDB TMN BESERI JAYA KAN00176 | PDB KAWAN SUPERMARKET KJT00415 - PMU TANJUNG PAUH TP15 | Insulation Breakdown | Insulation Deterioration | Conductor | CABLE | 05-08-2024 12:09 | 05-08-2024 12:25 | 16 | 28-09-2024 11:23 | 28-09-2024 22:06 | 10 | 28-09-2024 22:25 | 1318.4
Northern | K1 | TRIPPING-KED-24-00532 | 0242/20240806/040 | Kedah | Jitra | 11kV | Underground | 06-08-2024 16:42 | PMU TANJUNG PAUH TP15 | PMU TANJUNG PAUH TP15 | PBT KG. KUBANG PASU KJT00727 - | Open Circuit | Improper Installation | Cable XLPE | CABLE | 06-08-2024 16:56 | 06-08-2024 17:41 | 45 | 07-08-2024 01:03 | 08-08-2024 03:30 | 26 | 08-08-2024 04:05 | 35.38
Northern | K1 | TRIPPING-KED-24-00534 | 0242/20240807/062 | Kedah | Jitra | 11kV | Overhead | 07-08-2024 23:15 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01798 | PVCB SHOERUBBER KAN00740 - PDB SHOERUBBER LAMA KAN00742 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | NO FAULT | 07-08-2024 23:17 |  | 0 |  |  |  | 08-08-2024 00:37 | 1.37
Northern | K1 | TRIPPING-PLS-24-00068 | 2610/20240808/026 | Perlis | Perlis | 11kV | Underground | 07-08-2024 23:42 | PMU KANGAR CB13 | PVCB SHOERUBBER KAN00740 | PPU UUM SINTOK ST6 - PDB ASRAMA UUM KJT01019, - PDB ASRAMA UUM KJT01743 - SS BUKIT DAMAR KKN00597 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 07-08-2024 23:47 | 07-08-2024 23:50 | 3 | 16-08-2024 10:17 | 16-08-2024 22:23 | 12 | 16-08-2024 22:43 | 215.02
Northern | K1 | TRIPPING-KED-24-00537 | 0242/20240810/004 | Kedah | Jitra | 11kV | Underground | 10-08-2024 06:48 | PPU UUM SINTOK ST6 | PDB ASRAMA UUM KJT01743 | PDB KLG OTHMAN JUSOH KJT00044 - PLB KLG YUJAYA KJT00043 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE, CABLE | 10-08-2024 06:55 | 10-08-2024 08:00 | 65 | 10-08-2024 19:36, 10-08-2024 23:29, 10-08-2024 23:32, 10-08-2024 23:35, 13-08-2024 17:48, 17-08-2024 19:29, 17-08-2024 20:42 | 10-08-2024 21:26, 12-08-2024 21:17, 10-08-2024 23:33, 13-08-2024 16:15, 17-08-2024 17:29, 17-08-2024 20:21, 18-08-2024 13:58 | 1, 45, 0, 64, 95, 0, 17 | 18-08-2024 14:13 | 199.42
Northern | K1 | TRIPPING-KED-24-00539 | 0242/20240810/039 | Kedah | Jitra | 11kV | Underground | 10-08-2024 16:25 | PPU DARULAMAN 10K5 | STN SUIS 11KV IKBN JITRA KJT18896 | PPU POLITEKNIK PAUH PERLIS CB2 - | Open Circuit | Soil Movement | Cable XLPE | CABLE | 10-08-2024 17:24 | 10-08-2024 17:54 | 30 | 18-08-2024 10:57 | 18-08-2024 22:33 | 11 | 18-08-2024 22:56 | 198.52
Northern | K1 | TRIPPING-PLS-24-00069 | 2610/20240811/005 | Perlis | Perlis | 11kV | Underground | 11-08-2024 12:14 | PPU POLITEKNIK PAUH PERLIS 2 | PPU POLITEKNIK PAUH PERLIS CB2 | PDB TMN BUDAYA-KAN KAN02057 - HTL SRI MALAYSIA KANGAR KAN02045 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | NO FAULT | 11-08-2024 12:17 | 11-08-2024 12:45 | 28 |  |  |  | 11-08-2024 13:33 | 1.32
Northern | K1 | TRIPPING-PLS-24-00070 | 2610/20240813/015 | Perlis | Perlis | 11kV | Underground | 13-08-2024 08:58 | PMU KANGAR CB16 | SSU GIANT KGAR KAN02771 | PLB LPN LANA BULU KJT01312 - PATOD R/PAM MADA MEGAT DEWA KJT18985 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 13-08-2024 09:00 | 13-08-2024 09:30 | 30 | 20-08-2024 10:11 | 20-08-2024 22:09 | 11 | 20-08-2024 22:18 | 181.33
Northern | K1 | TRIPPING-KED-24-00545 | 0242/20240813/028 | Kedah | Jitra | 11kV | Underground | 13-08-2024 15:07 | PPU LOJI AIR ARAU GIS 12K5 | PPU LOJI AIR ARAU GIS 12K5 | TMN JELEMPOK JAYA KAN02766 - SEK KEBANGSAAN JELEMPOK KAN02534 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 13-08-2024 15:07 | 13-08-2024 15:45 | 38 | 13-08-2024 20:00 | 15-08-2024 16:29 | 44 | 15-08-2024 19:22 | 52.25
Northern | K1 | TRIPPING-PLS-24-00071 | 2610/20240814/018 | Perlis | Perlis | 11kV | Underground | 14-08-2024 10:09 | PPU LOJI AIR ARAU GIS 6K5 | PPU LOJI AIR ARAU GIS 6K5 | PATOD UJUNG BATU KAN01068 - PDB TMN MEDAN SEPAKAT-VVIP KAN00681 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 14-08-2024 10:11 | 14-08-2024 10:54 | 43 | 26-10-2024 11:52 | 27-10-2024 01:36 | 13 | 27-10-2024 01:50 | 1767.68
Northern | K1 | TRIPPING-PLS-24-00072 | 2610/20240815/022 | Perlis | Perlis | 11kV | Overhead | 15-08-2024 07:07 | PPU SIMPANG EMPAT CB3 | PPU SIMPANG EMPAT CB3 | PAT SMPG SG SIRAN KAN01417 - | Snapped | Hit by Vehicle | Conductor | OVERHEAD LINES | 15-08-2024 07:14 | 15-08-2024 07:45 | 31 | 15-08-2024 11:55 | 15-08-2024 22:42 | 10 | 15-08-2024 23:14 | 16.12
Northern | K1 | TRIPPING-PLS-24-00073 | 2610/20240820/005 | Perlis | Perlis | 11kV | Substation | 20-08-2024 07:12 | PPU MINI PPU ABI 11 | PPU MINI PPU ABI CB11 | PAT KG. KETUL KJT00083 - PDB KG. KETUL-KETUL (NOP) KJT00082 | Dielectric breakdown | Shorted By Animal | HV Cable (Tx Tail) | TRANSIENT | 20-08-2024 07:38 | 20-08-2024 08:00 | 22 |  |  |  | 20-08-2024 08:40 | 1.47
Northern | K1 | TRIPPING-KED-24-00560 | 0242/20240820/010 | Kedah | Jitra | 11kV | Underground | 20-08-2024 12:04 | PPU JERLUN SJ6 | A/R PIDA 5 | PDB HOSPITAL JITRA KJT00458 - PDB TNB JITRA KJT00457 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 20-08-2024 12:37 | 20-08-2024 13:20 | 43 | 20-08-2024 22:17 | 18-10-2024 02:24 | 1396 | 18-10-2024 02:44 | 1406.67
Northern | K1 | TRIPPING-KED-24-00562 | 0242/20240821/029 | Kedah | Jitra | 11kV | Underground | 21-08-2024 13:20 | PPU DARULAMAN 6K5 | PPU DARULAMAN 6K5 | PATOD KG. BARU PADONG KJT01068 - PLB FELDA BUKIT TANGGA KJT01067 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 21-08-2024 13:24 | 21-08-2024 13:45 | 21 | 21-08-2024 22:33 | 27-08-2024 02:17 | 123 | 27-08-2024 02:32 | 133.2
Northern | K1 | TRIPPING-KED-24-00575 | 0242/20240826/033 | Kedah | Jitra | 11kV | Underground | 26-08-2024 10:32 | PPU UUM SINTOK ST5 | S/S KLJ PERTANIAN BKT TANGGA KJT01848 | MEDAN BESERI INDAH KAN02951 - POLIKLINIK BESERI-VVIP KAN00305 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 26-08-2024 10:49 | 26-08-2024 11:20 | 31 | 27-08-2024 22:20 | 28-08-2024 20:56 | 22 | 28-08-2024 21:34 | 59.03
Northern | K1 | TRIPPING-PLS-24-00075 | 2610/20240828/061 | Perlis | Perlis | 11kV | Underground | 28-08-2024 15:54 | PMU KANGAR CB3 | POLIKLINIK BESERI-VVIP KAN00305 | PDB SK ARAU KAN00956 - KOMPLEK TOK ARAU KAN02860 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 28-08-2024 16:00 | 28-08-2024 16:36 | 36 | 03-09-2024 16:49 | 04-09-2024 00:26 | 7 | 04-09-2024 00:39 | 152.75
Northern | K1 | TRIPPING-PLS-24-00076 | 2610/20240831/023 | Perlis | Perlis | 11kV | Underground | 31-08-2024 00:23 | PPU LOJI AIR ARAU GIS 5K5 | PPU LOJI AIR ARAU GIS 5K5 | PAT MADA KURUNG ANAI - PPU LOJI AIR ARAU GIS 5K5 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 31-08-2024 00:27 | 31-08-2024 00:37 | 10 | 05-09-2024 21:01 | 06-09-2024 15:52 | 18 | 06-09-2024 16:22 | 159.98
Northern | K1 | TRIPPING-PLS-24-00077 | 2610/20240831/057 | Perlis | Perlis | 11kV | Underground | 31-08-2024 18:11 | PPU LOJI AIR ARAU GIS 5K5 | PPU LOJI AIR ARAU GIS 5K5 | PAT KUBANG JULOK KKN00368 - | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 31-08-2024 18:15 | 31-08-2024 18:45 | 30 | 02-09-2024 12:06 | 02-09-2024 22:58 | 10 | 02-09-2024 23:34 | 53.38
Northern | K1 | TRIPPING-KED-24-00589 | 0245/20240901/001 | Kedah | Kuala Nerang | 11kV | Substation | 01-09-2024 08:57 | PPU NAKA 4K5 | PPU NAKA 4K5 | STN SUIS KLG DXN KJT00246 - PLB KLG UBAT BKT WANG KJT00247 | Possible Animal | NA | Transient | TRANSIENT | 01-09-2024 08:58 | 01-09-2024 09:20 | 22 |  |  |  | 01-09-2024 10:30 | 1.55
Northern | K1 | TRIPPING-KED-24-00591 | 0242/20240901/044 | Kedah | Jitra | 11kV | Underground | 01-09-2024 12:28 | PPU DARULAMAN 3K5 | STN SUIS KLG DXN KJT00246 | PPU UNIMAP GIS 2K5 - FELDA CHUPING NO.2 KAN02680 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 01-09-2024 12:38 | 01-09-2024 13:00 | 22 | 01-09-2024 22:24 | 12-09-2024 22:52 | 264 | 12-09-2024 23:44 | 275.27
Northern | K1 | TRIPPING-PLS-24-00078 | 2610/20240905/009 | Perlis | Perlis | 11kV | Underground | 05-09-2024 05:53 | PPU UNIMAP GIS 2K5 | PPU UNIMAP GIS 2K5 | KEM PGA NO 1 KAN02914 - CSU BONDED ROAD 1 KAN03234 | - | - | Linkbox 11kV | CABLE | 05-09-2024 06:06 | 05-09-2024 06:11 | 5 | 09-09-2024 11:04 | 09-09-2024 22:06 | 11 | 09-09-2024 22:34 | 112.68
Northern | K1 | TRIPPING-PLS-24-00079 | 2610/20240905/015 | Perlis | Perlis | 11kV | Underground | 05-09-2024 07:47 | PPU PADANG BESAR CB12 | RPA PADANG BESAR KAN02910 | PMU KUALA PERLIS CB2 - TMN BUNGA PADI KAN01854 | Open Circuit | Improper Installation | Cable XLPE | CABLE | 05-09-2024 09:23 | 05-09-2024 09:54 | 31 | 11-09-2024 12:59 | 11-09-2024 20:22 | 7 | 11-09-2024 23:05 | 159.3
Northern | K1 | TRIPPING-PLS-24-00080 | 2610/20240907/062 | Perlis | Perlis | 11kV | Underground | 07-09-2024 18:30 | PMU KUALA PERLIS CB2 | PMU KUALA PERLIS CB2 | PAT PS 2 - PATOD R/PAM PS 1 KJT01163 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | OVERHEAD LINES | 07-09-2024 18:39 | 07-09-2024 19:05 | 26 | 19-09-2024 17:45 | 25-09-2024 22:57 | 149 | 25-09-2024 23:49 | 437.32
Northern | K1 | TRIPPING-KED-24-00606 | 0242/20240907/093 | Kedah | Jitra | 11kV | Overhead | 07-09-2024 20:09 | PPU KODIANG KD1 | PATOD R/PAM PS 1 KJT01163 | PAT KG. PADANG JELUTONG KAN00797 - SK PANGGAS KAN02285 | Insulation Breakdown | Insulation Deterioration | Conductor | CABLE | 07-09-2024 23:30 | 08-09-2024 01:18 | 108 | 08-09-2024 12:57, 09-09-2024 13:36 | 09-09-2024 11:53, 15-09-2024 21:29 | 22, 151 | 15-09-2024 21:55 | 193.77
Northern | K1 | TRIPPING-PLS-24-00081 | 2610/20240909/010 | Perlis | Perlis | 11kV | Overhead | 09-09-2024 02:57 | PMU CHUPING CB7 | PDB KUBANG PERUN KAN00255 | PBT KUALA SANGLANG 2 KJT01582 - PBT KUALA SANGLANG 1 KJT01581 | Insulation Breakdown | Insulation Deterioration | Conductor | CABLE | 09-09-2024 03:00 | 09-09-2024 03:40 | 40 | 06-10-2024 11:24 | 06-10-2024 23:42 | 12 | 07-10-2024 23:54 | 692.95
Northern | K1 | TRIPPING-KED-24-00609 | 0242/20240909/021 | Kedah | Jitra | 11kV | Underground | 09-09-2024 11:54 | PPU MINI PPU KERPAN KRPN 5K5 | PPU MINI PPU KERPAN KRPN 5K5 | PDB FLAT POLIS KANGAR KAN01837 - P/E TMN IRA JAYA KAN01838 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 09-09-2024 12:03 | 09-09-2024 12:25 | 22 | 09-09-2024 22:39 | 12-09-2024 21:31 | 70 | 12-09-2024 21:45 | 81.85
Northern | K1 | TRIPPING-PLS-24-00082 | 2610/20240909/054 | Perlis | Perlis | 11kV | Underground | 09-09-2024 14:24 | PMU KANGAR CB10 | PDB FLAT POLIS KANGAR KAN01837 | TAE HWA - PMU CHUPING CB8 |  |  |  | CABLE | 09-09-2024 14:25 | 09-09-2024 14:56 | 31 | 14-09-2024 08:47 | 14-09-2024 22:45 | 13 | 14-09-2024 23:00 | 128.6
Northern | K1 | TRIPPING-PLS-24-00083 | 2610/20240910/005 | Perlis | Perlis | 11kV | Underground | 10-09-2024 19:04 | PMU CHUPING CB8 | PMU CHUPING CB8 | P/P RENCAH NIAGA - PDB SK JITRA 2 KJT00383 |  |  |  | CABLE | 10-09-2024 19:40 | 10-09-2024 20:25 | 45 | 16-09-2024 00:53 | 18-09-2024 22:22 | 69 | 18-09-2024 22:31 | 195.45
Northern | K1 | TRIPPING-KED-24-00621 | 0242/20240912/009 | Kedah | Jitra | 11kV | Underground | 12-09-2024 07:46 | PMU TANJUNG PAUH TP19 | PMU TANJUNG PAUH TP19 | PBT KBG BETONG - PATOD CHANGKAT NIBONG KJT00739 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 12-09-2024 07:59 | 12-09-2024 08:11 | 12 | 13-09-2024 00:50 | 18-09-2024 02:03 | 121 | 18-09-2024 02:10 | 138.4
Northern | K1 | TRIPPING-KED-24-00622 | 0242/20240912/038 | Kedah | Jitra | 11kV | Underground | 12-09-2024 10:56 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01798 | PBT KBG BETONG - PATOD CHANGKAT NIBONG KJT00739 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 12-09-2024 10:58 | 12-09-2024 11:25 | 27 | 17-09-2024 09:58 | 24-09-2024 21:14 | 179 | 24-09-2024 21:46 | 298.83
Northern | K1 | TRIPPING-PLS-24-00084 | 2610/20240912/017 | Perlis | Perlis | 11kV | Overhead | 12-09-2024 11:28 | PPU BUKIT KETERI 3K5 | PVCB PANGGAS KAN00281 |  | Insulation Breakdown | Insulation Deterioration | Cable Termination | TRANSIENT | 12-09-2024 11:40 | 12-09-2024 12:15 | 35 |  |  |  | 12-09-2024 13:05 | 1.62
Northern | K1 | TRIPPING-KED-24-00623 | 0242/20240912/061 | Kedah | Jitra | 11kV | Underground | 12-09-2024 16:29 | PPU JERLUN SJ1 | SM SANGLANG KJT01475 | PDB KUATERS GURU SM SANGLANG KJT19405 - PDB KLG BERAS EVERGREEN KJT01575 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 12-09-2024 16:31 | 12-09-2024 16:58 | 27 | 13-09-2024 00:57 | 18-09-2024 20:28 | 139 | 18-09-2024 20:59 | 148.5
Northern | K1 | TRIPPING-KED-24-00627 | 0245/20240914/024 | Kedah | Kuala Nerang | 11kV | Underground | 14-09-2024 13:01 | PPU KUALA NERANG 3K5 | A/R KG. TENGAH | PATOD KG.BUKIT PERIK KKN00245 - PBT KG. PERIK KKN00247 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 14-09-2024 13:08 | 14-09-2024 13:30 | 22 | 14-09-2024 22:39 | 15-09-2024 23:24 | 24 | 15-09-2024 23:40 | 34.65
Northern | K1 | TRIPPING-PLS-24-00085 | 2610/20240914/047 | Perlis | Perlis | 11kV | Underground | 14-09-2024 21:35 | PMU KANGAR CB2 | PDB TELEKOM LAMA KANGAR KAN00548 | PDB TELEKOM LAMA KANGAR KAN00548 - HOSPITAL TUANKU FAUZIAH KAN02622 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 14-09-2024 21:38 | 14-09-2024 21:54 | 16 | 19-09-2024 10:57 | 20-09-2024 16:33 | 29 | 20-09-2024 16:37 | 139.03
Northern | K1 | TRIPPING-KED-24-00636 | 0242/20240917/224 | Kedah | Jitra | 11kV | Overhead | 17-09-2024 21:46 | PPU DARULAMAN 4K5 | RUMAH KEDAI 50 UNIT KJT19301 | PAT KG. PDG LIMAU KJT18367 - PAT KG GELONG RAMBAI KJT01743 | Insulation Breakdown | Insulation Deterioration | Conductor | CABLE | 17-09-2024 21:51 | 17-09-2024 22:30 | 39 | 18-09-2024 00:23, 18-09-2024 21:46 | 18-09-2024 06:45, 19-09-2024 15:44 | 6, 17 | 19-09-2024 16:50 | 43.07
Northern | K1 | TRIPPING-KED-24-00640 | 0242/20240918/156 | Kedah | Jitra | 11kV | Underground | 18-09-2024 12:34 | PMU TANJUNG PAUH TP15 | PMU TANJUNG PAUH TP15 | PMUTANJUNG PAUH TP15 - PDB KAWAN SUPERMARKET KJT00415 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 18-09-2024 12:42 | 18-09-2024 13:20 | 38 | 18-09-2024 21:48 | 08-10-2024 09:15 | 467 | 08-10-2024 09:52 | 477.3
Northern | K1 | TRIPPING-KED-24-00647 | 0242/20240920/002 | Kedah | Jitra | 11kV | Underground | 20-09-2024 00:15 | PPU JERLUN SJ4 | SSBT PERMATANG GELOK KJT01548 | PAT PERMATANG GELOK - SSBT PERMATANG GELOK KJT01548 |  |  |  | CABLE | 20-09-2024 00:30 | 20-09-2024 00:45 | 15 | 20-09-2024 22:09 | 22-09-2024 21:14 | 47 | 22-09-2024 21:50 | 69.58
Northern | K1 | TRIPPING-KED-24-00653 | 0245/20240920/022 | Kedah | Kuala Nerang | 11kV | Underground | 20-09-2024 16:36 | PPU NAKA 6K5 | PPU NAKA 6K5 | PLB KEDA KG. BAGAN KKN00427 - PBT KG. LUBOK RAMBAI KKN00623 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 20-09-2024 16:44 | 20-09-2024 17:23 | 39 | 20-09-2024 22:41 | 21-09-2024 23:49 | 25 | 22-09-2024 00:15 | 31.65
Northern | K1 | TRIPPING-PLS-24-00087 | 2610/20240921/008 | Perlis | Perlis | 11kV | Underground | 21-09-2024 07:17 | PMU KANGAR CB13 | PMU KANGAR CB13 | PMU KANGAR CB13 - PVCB SHOERUBBER KAN00738 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 21-09-2024 07:21 | 21-09-2024 07:33 | 12 | 13-10-2024 18:18 | 14-10-2024 12:58 | 18 | 14-10-2024 13:14 | 557.95
Northern | K1 | TRIPPING-KED-24-00657 | 0242/20240923/018 | Kedah | Jitra | 11kV | Underground | 23-09-2024 11:44 | PPU DARULAMAN 8K5 | PPU DARULAMAN 8K5 | PBT DRIVING RANGE KJT00212 - PDB TMN GOLF NO4 KJT00213 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 23-09-2024 11:49 | 23-09-2024 12:13 | 24 | 23-09-2024 22:03 | 25-09-2024 21:47 | 47 | 25-09-2024 22:07 | 58.38
Northern | K1 | TRIPPING-PLS-24-00088 | 2610/20240923/058 | Perlis | Perlis | 11kV | Overhead | 23-09-2024 13:34 | PPU PADANG BESAR CB2 | FISHING NET KAN00068 | PLB LUBUK SIREH 2 KAN02270 - PEKAN SAYUR PEKAN KAKI BUKIT KAN02349 | Insulation Breakdown | Insulation Deterioration | Conductor | CABLE | 23-09-2024 13:48 | 23-09-2024 14:25 | 37 | 26-09-2024 11:40 | 26-09-2024 21:51 | 10 | 26-09-2024 22:08 | 80.57
Northern | K1 | TRIPPING-KED-24-00662 | 0245/20240925/001 | Kedah | Kuala Nerang | 11kV | Overhead | 25-09-2024 05:36 | PPU KUALA NERANG 7K5 | PPU KUALA NERANG 7K5 | PEJ DAERAH BARU KKN00520 - PDB TMN MERBAU-KNRG KKN00657 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 25-09-2024 05:43 | 25-09-2024 06:40 | 57 | 25-09-2024 18:07 | 28-09-2024 21:16 | 75 | 28-09-2024 21:40 | 88.07
Northern | K1 | TRIPPING-PLS-24-00089 | 2610/20240926/034 | Perlis | Perlis | 11kV | Underground | 26-09-2024 14:39 | PPU PADANG BESAR CB11 | PPU PADANG BESAR CB11 | PDB HALAL HUB KAN02416 - SK FELDA RIMBA MAS KAN02414 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 26-09-2024 14:41 | 26-09-2024 15:02 | 21 |  |  |  | 30-09-2024 22:50 | 104.18
Northern | K1 | TRIPPING-KED-24-00669 | 0242/20240928/012 | Kedah | Jitra | 11kV | Underground | 28-09-2024 02:27 | PPU MINI PPU KERPAN KRPN 5K5 | PPU MINI PPU KERPAN KRPN 5K5 | PBT KUALA SANGLANG 2 KJT01582 - PBT KUALA SANGLANG 1 KJT01581 | Open Circuit | Improper Installation | Cable XLPE | CABLE | 28-09-2024 02:30 | 28-09-2024 03:15 | 45 | 28-09-2024 22:27 | 29-09-2024 22:26 | 23 | 29-09-2024 22:41 | 44.23
Northern | K1 | TRIPPING-PLS-24-00090 | 2610/20240928/171 | Perlis | Perlis | 11kV | Underground | 28-09-2024 22:43 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 | PDB RPA JEJAWI KAN00758 - PDB TMN GEMBIRA-KAN KAN02235, - PBT MADA JEJAWI SEMATANG KAN00981 - CSU RUMAH PAM JEJAWI KAN03189 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE, CABLE | 28-09-2024 23:01 | 28-09-2024 23:20 | 19 | 05-10-2024 10:03, 07-11-2024 10:44 | 06-10-2024 00:28, 08-11-2024 01:11 | 14, 14 | 08-11-2024 01:23 | 962.67
Northern | K1 | TRIPPING-KED-24-00672 | 0245/20240929/053 | Kedah | Kuala Nerang | 11kV | Underground | 29-09-2024 20:57 | PPU KUALA NERANG 6K5 | PPU KUALA NERANG 6K5 | PBT KG. BENDANG RAJA KKN00200 - STESEN SUIS FELCRA BELIMBING KKN00202 | Insulation Breakdown | Insulation Deterioration | Cable PILC | NO FAULT | 29-09-2024 21:10 | 29-09-2024 21:24 | 14 | 30-09-2024 15:32 | 01-10-2024 22:58 | 31 | 02-10-2024 00:20 | 51.38
Northern | K1 | TRIPPING-PLS-24-00091 | 2610/20241007/073 | Perlis | Perlis | 11kV | Substation | 07-10-2024 21:47 | PPU SHORUBBER CB3 | PPU SHORUBBER CB3 | PDB MIEL KUKUM JEJAWI KAN00733 - | Dielectric | Moisture | Circuit Breaker | SWITCHGEAR | 07-10-2024 21:53 | 07-10-2024 22:20 | 27 | 11-10-2024 09:21 | 11-10-2024 23:39 | 14 | 12-10-2024 00:47 | 99
Northern | K1 | TRIPPING-PLS-24-00092 | 2610/20241008/006 | Perlis | Perlis | 11kV | Underground | 08-10-2024 02:11 | PPU BUKIT KETERI 3K5 | PPU BUKIT KETERI 3K5 | PPU BUKIT KETERI 3K5 - PVCB PANGGAS KAN00280 | Open Circuit | Soil Movement | Straight Through Joint | CABLE | 08-10-2024 02:20 | 08-10-2024 02:51 | 31 | 16-10-2024 11:28 | 16-10-2024 23:49 | 12 | 16-10-2024 23:55 | 213.73
Northern | K1 | TRIPPING-KED-24-00707 | 0245/20241008/005 | Kedah | Kuala Nerang | 11kV | Underground | 08-10-2024 06:15 | PPU KUALA NERANG 3K5 | A/R KG. TENGAH | PAT KG. BAYAS-ALS KKN00256 - PBT KG. PERIK KKN00248 | Insulation Breakdown | Insulation Deterioration | Straight Through Joint | CABLE | 08-10-2024 06:16 | 08-10-2024 06:50 | 34 | 08-10-2024 12:07 | 10-10-2024 21:44 | 57 | 10-10-2024 23:35 | 65.33
Northern | K1 | TRIPPING-PLS-24-00096 | 2610/20241010/016 | Perlis | Perlis | 11kV | Underground | 10-10-2024 11:21 | PPU SIMPANG EMPAT CB5 | SEK MEN SANGLANG KAN01095 | PDB KOLAM UDANG YAYASAN ISLAM KAN01131 - PDB K/UDANG RAMADIN KAN01130 | Open Circuit | Soil Movement | Transition Joint | CABLE | 10-10-2024 11:25 | 10-10-2024 12:05 | 40 | 20-10-2024 11:13 | 20-10-2024 23:22 | 12 | 20-10-2024 23:30 | 252.15
Northern | K1 | TRIPPING-PLS-24-00097 | 2610/20241015/037 | Perlis | Perlis | 11kV | Underground | 15-10-2024 17:43 | PMU CHUPING CB6 | PMU CHUPING CB6 | FELDA CHUPING NO.2 KAN02698 - PDB KOK KELANG 2 KAN00250 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 15-10-2024 17:49 | 15-10-2024 18:16 | 27 | 28-10-2024 11:01 | 03-11-2024 23:07 | 156 | 03-11-2024 23:28 | 461.75
Northern | K1 | TRIPPING-PLS-24-00098 | 2610/20241016/024 | Perlis | Perlis | 11kV | Underground | 16-10-2024 09:16 | PPU SHORUBBER CB5 | PPU SHORUBBER CB5 | PAT KEPALA 20 BEHOR GELAM KAN00978 - PAT BEHOR GELAM KAN00979 | Open Circuit | Soil Movement | Transition Joint | CABLE | 16-10-2024 09:30 | 16-10-2024 09:55 | 25 | 17-10-2024 00:45 | 17-10-2024 23:49 | 23 | 18-10-2024 00:35 | 39.32
Northern | K1 | TRIPPING-KED-24-00737 | 0242/20241017/050 | Kedah | Jitra | 11kV | Underground | 17-10-2024 19:29 | PPU KODIANG KD2 | PDB SM TUNKU BENDAHARA KJT01255 | PAT GUAR BATU HITAM KJT01272 - PLD FELDA BATU 8 CHANGLUN KJT19117 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 17-10-2024 19:37 | 17-10-2024 20:13 | 36 | 18-10-2024 22:19 | 22-10-2024 22:04 | 95 | 22-10-2024 22:24 | 122.92
Northern | K1 | TRIPPING-KED-24-00741 | 0242/20241021/047 | Kedah | Jitra | 11kV | Underground | 21-10-2024 02:40 | PMU BUKIT KAYU HITAM BKH4 | PDB PROTAB AGROBASE KJT01140 | SSD NO.1 KJT01142 - PAT BATU 26 KJT19463 | Open Circuit | Soil Movement | Straight Through Joint | CABLE | 21-10-2024 02:44 | 21-10-2024 03:20 | 36 | 21-10-2024 22:03 | 24-10-2024 00:26 | 50 | 24-10-2024 01:00 | 70.33
Northern | K1 | TRIPPING-KED-24-00748 | 0242/20241024/018 | Kedah | Jitra | 11kV | Underground | 24-10-2024 11:05 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01798 | PATOD CHANGKAT NIBONG KJT00739 - PBT KBG BETONG KJT00738 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 24-10-2024 11:12 | 24-10-2024 11:33 | 21 | 24-10-2024 22:41 | 28-10-2024 20:32 | 93 | 13-01-2025 21:49 | 1954.73
Northern | K1 | TRIPPING-PLS-24-00099 | RE/2610/20241028/PLS/00099 | Perlis | Perlis | 11kV | underground | 28-10-2024 05:06 | PPU BUKIT KETERI 1K5 | PDB TMN SRI PUTERI KAN02605 | RE(RSO) OUTREACH GREEN 1 B1 - |  |  |  | CABLE | 28-10-2024 05:11 | 28-10-2024 05:53 | 42 |  |  |  | 28-10-2024 12:50 | 7.73
Northern | K1 | TRIPPING-PLS-24-00100 | 2610/20241028/041 | Perlis | Perlis | 11kV | Overhead | 28-10-2024 16:14 | PPU PADANG BESAR CB10 | SSU MRCB CVIA KAN03298 | TPK PELUPUSAN SAMPAH RIMBA MAS - PBT CHECK POINT KAN00094 | Insulation Breakdown | Old External Damage | Conductor | CABLE | 28-10-2024 16:19 | 28-10-2024 17:04 | 45 | 18-11-2024 11:31 | 18-11-2024 23:04 | 11 | 18-11-2024 23:52 | 511.63
Northern | K1 | TRIPPING-KED-24-00765 | 0242/20241029/002 | Kedah | Jitra | 11kV | Underground | 29-10-2024 02:56 | PPU KODIANG KD2 | PDB SM TUNKU BENDAHARA KJT01255 | SSBT KG. LIMAU BALI KJT01269 - PLD FELDA BATU 8 CHANGLUN KJT19117 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 29-10-2024 02:58 | 29-10-2024 03:56 | 58 | 29-10-2024 22:18 | 30-10-2024 22:43 | 24 | 30-10-2024 22:57 | 44.02
Northern | K1 | TRIPPING-PLS-24-00101 | 2610/20241101/014 | Perlis | Perlis | 11kV | Substation | 01-11-2024 12:50 | PMU CHUPING CB1 | PLB KAJI CUACA KAN00789 | PAT SG. MATI-KAN KAN01598 - | Dielectric breakdown | Animal | HV Cable (Tx Tail) | NO FAULT | 01-11-2024 13:08 | 01-11-2024 13:24 | 16 |  |  |  | 01-11-2024 13:49 | 0.98
Northern | K1 | TRIPPING-KED-24-00771 | 0245/20241101/022 | Kedah | Kuala Nerang | 11kV | Overhead | 01-11-2024 23:02 | PPU MINI PPU L/AIR PDG SANAI LA3 | PPU MINI PPU L/AIR PDG SANAI LA3 | LDG SG SERAYA KKN00772 - PDB LOJI AIR PADANG SANAI KKN00318 | Insulation Breakdown | Insulation Deterioration | Conductor | CABLE | 01-11-2024 23:03 | 01-11-2024 23:33 | 30 | 02-11-2024 17:28 | 04-11-2024 03:31 | 34 | 04-11-2024 03:55 | 52.88
Northern | K1 | TRIPPING-PLS-24-00102 | 2610/20241102/070 | Perlis | Perlis | 11kV | Underground | 02-11-2024 18:47 | PPU SHORUBBER CB4 | PVCB TMN JALI KAN02329 | PDB TMN KEMAJUAN 1 KAN00582 - PDB TMN KEMAJUAN 2 KAN00581 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 02-11-2024 18:49 | 02-11-2024 19:30 | 41 | 04-11-2024 21:05, 12-11-2024 18:46 | 05-11-2024 09:16, 13-11-2024 09:03 | 12, 14 | 13-11-2024 09:18 | 254.52
Northern | K1 | TRIPPING-KED-24-00774 | 0245/20241102/022 | Kedah | Kuala Nerang | 11kV | Underground | 02-11-2024 19:52 | PPU KUALA NERANG 3K5 | A/R KG. TENGAH | PATOD KG.BUKIT PERIK KKN00245 - PBT KG. PERIK KKN00247 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 02-11-2024 19:58 | 02-11-2024 20:19 | 21 | 03-11-2024 16:40 | 06-11-2024 00:12 | 55 | 06-11-2024 00:38 | 76.77
Northern | K1 | TRIPPING-PLS-24-00103 | 2610/20241103/008 | Perlis | Perlis | 11kV | Underground | 03-11-2024 10:51 | PPU MINI PPU ABI 1K5 | PPU MINI PPU ABI 1K5 | PDB SMPG ABI KAN00316 - PLB KUARI BATU TEONG CHAI KAN00317 | Open Circuit | Soil Movement | Transition Joint | CABLE | 03-11-2024 12:55 | 03-11-2024 14:13 | 78 | 09-11-2024 10:16 | 09-11-2024 23:13 | 12 | 09-11-2024 23:35 | 156.73
Northern | K1 | TRIPPING-KED-24-00793 | 0242/20241112/031 | Kedah | Jitra | 11kV | Underground | 12-11-2024 15:13 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01798 | PBT KBG BETONG KJT00738 - PATOD CHANGKAT NIBONG KJT00739 | Open Circuit | Soil Movement | Transition Joint | CABLE | 12-11-2024 15:16 | 12-11-2024 15:48 | 32 | 12-11-2024 22:37, 14-11-2024 09:55, 14-11-2024 22:32 | 13-11-2024 02:18, 14-11-2024 22:21, 19-11-2024 22:21 | 3, 12, 119 | 19-11-2024 22:25 | 175.2
Northern | K1 | TRIPPING-PLS-24-00104 | 2610/20241113/024 | Perlis | Perlis | 11kV | Underground | 13-11-2024 15:11 | PMU KUALA PERLIS CB8 | PDB TMN BUMITA KAN00597 CB1 | TMN GUNUNG MEDAN - PDB TMN MEDAN SEPAKAT | Open Circuit | Soil Movement | Cable XLPE | CABLE | 13-11-2024 15:14 | 13-11-2024 15:50 | 36 | 14-11-2024 11:08 | 14-11-2024 22:07 | 10 | 14-11-2024 22:23 | 31.2
Northern | K1 | TRIPPING-PLS-24-00106 | RE/2610/20241116/PLS/00106 | Perlis | Perlis | 11kV | Underground | 16-11-2024 18:50 | PPU UNIMAP GIS 1K5 | SSD UNIMAP ULU PAUH KAN02786 |  |  |  | Cable PILC | CABLE | 16-11-2024 19:40 | 16-11-2024 20:05 | 25 |  |  |  | 17-11-2024 17:35 | 22.75
Northern | K1 | TRIPPING-PLS-24-00107 | 2610/20241117/049 | Perlis | Perlis | 11kV | Underground | 17-11-2024 10:38 | PPU BUKIT KETERI 6K5 | PDB TMN BESERI JAYA KAN00178 CB1 | PDB KMPL PERTANIAN BKT TEMIANG - PDB TMN BESERI PERMAI KAN00201 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 17-11-2024 10:51 | 17-11-2024 11:30 | 39 | 23-11-2024 10:21 | 23-11-2024 23:04 | 12 | 23-11-2024 23:18 | 156.67
Northern | K1 | TRIPPING-KED-24-00826 | 0242/20241121/094 | Kedah | Jitra | 11kV | Underground | 21-11-2024 22:59 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01798 CB1 | PBT KBG BETONG - PATOD CHANGKAT NIBONG KJT00739 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 21-11-2024 23:03 | 21-11-2024 23:13 | 10 | 22-11-2024 21:58 | 24-11-2024 21:13 | 47 | 24-11-2024 21:20 | 70.35
Northern | K1 | TRIPPING-PLS-24-00108 | 2610/20241122/004 | Perlis | Perlis | 11kV | Underground | 22-11-2024 05:53 | PMU KANGAR CB1 | PDB SEKOLAH VOKASIONAL KANGAR KAN00472 CB1 | PDB SK SRI INDRA KAN00470 - PDB PERPUSTAKAAN NEGERI-PPNPS KAN00469 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 22-11-2024 05:57 | 22-11-2024 06:30 | 33 | 26-11-2024 10:40 | 26-11-2024 22:45 | 12 | 26-11-2024 22:55 | 113.03
Northern | K1 | TRIPPING-PLS-24-00109 | 2610/20241124/029 | Perlis | Perlis | 11kV | Underground | 24-11-2024 09:07 | PMU CHUPING CB1 | PMU CHUPING CB1 | PAT BAWAH BUKIT KAN00267 - PDB INFANTRI BATALION KAN00795 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 24-11-2024 09:09 | 24-11-2024 09:50 | 41 | 27-11-2024 11:44 | 27-11-2024 23:39 | 11 | 27-11-2024 23:50 | 86.72
Northern | K1 | TRIPPING-KED-24-00843 | 0242/20241128/007 | Kedah | Jitra | 11kV | Underground | 28-11-2024 04:02 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01798 CB1 | PBT KBG BETONG - PATOD CHANGKAT NIBONG KJT00739 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 28-11-2024 04:09 | 28-11-2024 04:50 | 41 | 28-11-2024 21:19 | 02-12-2024 17:36 | 92 | 02-12-2024 17:42 | 109.67
Northern | K1 | TRIPPING-KED-24-00845 | 0245/20241128/032 | Kedah | Kuala Nerang | 11kV | Underground | 28-11-2024 18:24 | PPU KUALA NERANG 6K5 | PPU KUALA NERANG 6K5 | PBT KG. BENDANG RAJA KKN00200 - STESEN SUIS FELCRA BELIMBING KKN00202 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 28-11-2024 18:30 | 28-11-2024 19:05 | 35 | 05-12-2024 11:06 | 05-12-2024 19:42 | 8 | 05-12-2024 20:20 | 169.93
Northern | K1 | TRIPPING-PLS-24-00110 | 2610/20241201/005 | Perlis | Perlis | 11kV | Underground | 01-12-2024 10:37 | PMU CHUPING CB6 | PMU CHUPING CB6 | PDB KOK KELANG 2 KAN00250 - FELDA CHUPING NO.2 KAN02698 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 01-12-2024 10:58 | 01-12-2024 11:38 | 40 | 03-12-2024 11:00 | 03-12-2024 22:13 | 11 | 03-12-2024 22:38 | 60.02
Northern | K1 | TRIPPING-KED-24-00861 | 0243/20241204/032 | Kedah | Jitra | 11kV | Underground | 04-12-2024 00:22 | PPU CHANGLOON CL4 | PPU CHANGLOON CL4 | TMN JELUTONG FASA 2 KJT19192 - C/SUB TAMAN NAPOH KJT19292 | Insulation Breakdown | Mechanical damage due to old external wound | Cable PILC | CABLE | 04-12-2024 00:25 | 04-12-2024 01:00 | 35 | 04-12-2024 22:22 | 05-12-2024 19:00 | 20 | 05-12-2024 19:41 | 43.32
Northern | K1 | TRIPPING-KED-24-00863 | 0242/20241204/072 | Kedah | Jitra | 11kV | Underground | 04-12-2024 16:36 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00742 CB1 | PATOD CHANGKAT NIBONG KJT00739 - PBT KBG BETONG KJT00738 | Insulation Breakdown | Mechanical damage due to old external wound | Cable PILC | CABLE | 04-12-2024 16:38 | 04-12-2024 17:10 | 32 | 04-12-2024 18:13 | 10-12-2024 12:32 | 138 | 10-12-2024 12:58 | 140.37
Northern | K1 | TRIPPING-KED-24-00882 | 0242/20241211/005 | Kedah | Jitra | 11kV | Underground | 11-12-2024 08:22 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01798 CB1 | PBT KBG BETONG KJT00738 - PATOD CHANGKAT NIBONG KJT00739 | Insulation Breakdown | Mechanical damage due to old external wound | Cable PILC | CABLE | 11-12-2024 08:27 | 11-12-2024 08:50 | 23 | 11-12-2024 09:25, 14-12-2024 22:14 | 12-12-2024 21:06, 16-12-2024 18:54 | 35, 44 | 16-12-2024 19:02 | 130.67
Northern | K1 | TRIPPING-PLS-24-00112 | 2610/20241211/008 | Perlis | Perlis | 11kV | Underground | 11-12-2024 10:41 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 - PDB TMN SEMATANG JAYA KAN00985 | Open Circuit | Improper Installation | Cable XLPE | CABLE | 11-12-2024 10:45 | 11-12-2024 10:53 | 8 | 11-12-2024 15:06 | 12-12-2024 09:19 | 18 | 12-12-2024 09:34 | 22.88
Northern | K1 | TRIPPING-PLS-24-00113 | 2610/20241211/047 | Perlis | Perlis | 11kV | Underground | 11-12-2024 15:15 | PPU SHORUBBER CB6 | PDB POLIKLINIK ARAU KAN00902 CB1 |  |  |  |  | NO FAULT | 11-12-2024 15:18 | 11-12-2024 16:00 | 42 |  |  |  | 11-12-2024 18:43 | 3.47
Northern | K1 | TRIPPING-KED-24-00893 | 0242/20241216/028 | Kedah | Jitra | 11kV | Underground | 16-12-2024 10:59 | PPU LOJI AIR ARAU GIS 11K5 | PDB KLG BERAS PERING KJT01776 CB1 | PBT(PATOD) BATU 4 SANGLANG KJT01400 - PBT BATU 5 KJT01399 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 16-12-2024 11:02 | 16-12-2024 11:43 | 41 | 16-12-2024 12:09, 16-12-2024 12:30 | 16-12-2024 12:28, 19-12-2024 18:48 | 0, 78 | 19-12-2024 19:34 | 80.58
Northern | K1 | TRIPPING-KED-24-00895 | 0242/20241217/025 | Kedah | Jitra | 11kV | Underground | 17-12-2024 18:30 | PPU DARULAMAN 1K5 | SEK MEN CHANGLUN KJT00742 CB1 | PATOD CHANGKAT NIBONG KJT00739 - PBT KBG BETONG KJT00738 | Insulation Breakdown | Mechanical damage due to old external wound | Cable PILC | CABLE | 17-12-2024 18:34 | 17-12-2024 19:00 | 26 | 17-12-2024 23:19 | 23-12-2024 21:49 | 142 | 23-12-2024 21:54 | 147.4
Northern | K1 | TRIPPING-PLS-24-00114 | 2610/20241218/001 | Perlis | Perlis | 11kV | Underground | 18-12-2024 01:20 | PMU KANGAR CB12 | PVCB TMN MERPATI KAN03103 CB1 | PDB PERINDUSTRIAN RINGAN KAN00726 - ADVANCE CHICKEN KAN02352 | Open Circuit | Soil Movement | Transition Joint | CABLE | 18-12-2024 01:22 | 18-12-2024 01:55 | 33 | 22-12-2024 10:26 | 22-12-2024 22:59 | 12 | 22-12-2024 23:11 | 117.85
Northern | K1 | TRIPPING-PLS-24-00115 | 2610/20241218/007 | Perlis | Perlis | 11kV | Substation | 18-12-2024 07:57 | PPU LOJI AIR ARAU GIS 8K5 | PVCB RUMAH PAM GUAR SANJI KAN00958 | PAT KG. BANAT KAN00969 - | Dielectric breakdown | Shorted By Animal | HV Cable (Tx Tail) | NO FAULT | 18-12-2024 07:59 | 18-12-2024 08:30 | 31 |  |  |  | 18-12-2024 09:07 | 1.17
Northern | K1 | TRIPPING-KED-24-00899 | 0242/20241218/030 | Kedah | Jitra | 11kV | Overhead | 18-12-2024 12:17 | PPU CHANGLOON CL4 | PPU CHANGLOON CL4 | TMN JELUTONG FASA 2 KJT19192 - C/SUB TAMAN NAPOH KJT19292 | Insulation Breakdown | Insulation Deterioration | Conductor | CABLE | 18-12-2024 12:20 | 18-12-2024 12:50 | 30 | 18-12-2024 15:48 | 18-12-2024 21:16 | 5 | 18-12-2024 21:26 | 9.15
Northern | K1 | TRIPPING-KED-24-00905 | 0242/20241219/052 | Kedah | Jitra | 11kV | Overhead | 19-12-2024 01:00 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00895 CB1 | PLB RUMAH PAM KG.TEBING KJT00913 - KG. LEMBAH KJT00912 | Insulation Breakdown | Insulation Deterioration | Conductor | CABLE | 19-12-2024 01:03 | 19-12-2024 01:33 | 30 | 19-12-2024 22:58 | 22-12-2024 00:17 | 49 | 22-12-2024 00:55 | 71.92
Northern | K1 | TRIPPING-KED-24-00917 | 0242/20241220/037 | Kedah | Jitra | 11kV | Overhead | 20-12-2024 23:55 | PPU CHANGLOON CL4 | PPU CHANGLOON CL4 | C/SUB TAMAN NAPOH - TMN JELUTONG FASA 2 KJT19192 | Insulation Breakdown | Old External Damage | Conductor | CABLE | 21-12-2024 00:06 | 21-12-2024 00:25 | 19 | 21-12-2024 23:33 | 22-12-2024 22:56 | 23 | 22-12-2024 23:02 | 47.12
Northern | K1 | TRIPPING-PLS-24-00116 | 2610/20241222/013 | Perlis | Perlis | 11kV | Underground | 22-12-2024 03:38 | PMU KANGAR CB6 | PMU KANGAR CB6 | VETERINAR KANGAR KAN02974 - TMN SRI HARTAMAS KAN02903 | Insulation Breakdown | Mechanical damage due to old external wound | Cable PILC | CABLE | 22-12-2024 03:41 | 22-12-2024 04:00 | 19 | 07-01-2025 21:28 | 16-01-2025 08:28 | 202 | 16-01-2025 08:47 | 605.15
Northern | K1 | TRIPPING-KED-24-00922 | 0242/20241222/028 | Kedah | Jitra | 11kV | Underground | 22-12-2024 16:47 | PMU BUKIT KAYU HITAM BKH8 | STN SUIS ICQS KJT19258 | PDB KOMP BEBAS CUKAI KJT01109 - PDB RUMAH KELAB BLACKFOREST KJT01110 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 22-12-2024 17:15 | 22-12-2024 17:28 | 13 | 26-12-2024 12:14 | 26-12-2024 20:41 | 8 | 26-12-2024 20:50 | 100.05
Northern | K1 | TRIPPING-KED-24-00932 | 0242/20241228/049 | Kedah | Jitra | 11kV | Underground | 28-12-2024 11:04 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00895 CB1 | PBT KG. BATAS KJT19123 - PLB RUMAH PAM KG.TEBING KJT19122 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable PILC | CABLE | 28-12-2024 11:07 | 28-12-2024 11:42 | 35 | 28-12-2024 16:45 | 01-01-2025 22:25 | 101 | 01-01-2025 23:44 | 108.67
Northern | K1 | TRIPPING-KED-24-00933 | 0242/20241228/077 | Kedah | Jitra | 11kV | Underground | 28-12-2024 12:34 | PPU CHANGLOON CL4 | PPU CHANGLOON CL4 | TMN JELUTONG FASA 2 KJT19192 - C/SUB TAMAN NAPOH KJT19292 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable PILC | CABLE | 28-12-2024 12:36 | 28-12-2024 13:02 | 26 | 28-12-2024 20:07 | 31-12-2024 13:59 | 65 | 01-01-2025 14:34 | 98
Northern | K1 | TRIPPING-PLS-24-00118 | 2610/20241229/007 | Perlis | Perlis | 11kV | Underground | 29-12-2024 05:35 | PMU KANGAR CB16 | PVCB TMN JALI KAN02326 CB1 | PDB LOT 42 TMN BUKIT KAYA KAN00561 - MEDAN NIAGA KANGAR KAN02715 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 29-12-2024 05:40 | 29-12-2024 06:15 | 35 | 31-12-2024 10:52 | 31-12-2024 23:30 | 12 | 31-12-2024 23:48 | 66.22
Northern | K1 | TRIPPING-PLS-24-00119 | 2610/20241230/041 | Perlis | Perlis | 11kV | Underground | 30-12-2024 01:50 | PMU KUALA PERLIS CB1 | PMU KUALA PERLIS CB1 |  | Insulation Breakdown | Mechanical damage due to old external wound | RMU SF6 | SWITCHGEAR | 30-12-2024 02:10 | 30-12-2024 02:25 | 15 | 04-01-2025 10:50 | 05-01-2025 23:30 | 36 | 05-01-2025 23:43 | 165.88
Northern | K1 | TRIPPING-KED-25-00001 | 0242/20250101/009 | Kedah | Jitra | 11kV | Underground | 01-01-2025 14:25 | PMU BUKIT KAYU HITAM BKH8 | STN SUIS ICQS KJT19258 | PDB KOMP BEBAS CUKAI KJT01109 - PDB RUMAH KELAB BLACKFOREST KJT01110 | Open Circuit | Soil Movement | Transition Joint | CABLE | 01-01-2025 15:00 | 01-01-2025 15:23 | 23 | 01-01-2025 16:05 | 02-01-2025 20:43 | 28 | 02-01-2025 20:58 | 30.55 | 169.9m | 164.3m | 177.9m | 232m | 211m | 240m | 1.38 | 13 | 1.35
Northern | K1 | TRIPPING-PLS-25-00001 | 2610/20250105/017 | Perlis | Perlis | 11kV | Underground | 05-01-2025 07:23 | PPU BUKIT KETERI 3K5 | PVCB PANGGAS KAN00281 CB1 | PAT SEMADONG KAN01796 - | Insulation Breakdown | Insulation Deterioration | Cable PILC | TRANSIENT | 05-01-2025 07:30 | 05-01-2025 08:01 | 31 |  |  |  | 05-01-2025 08:55 | 1.53
Northern | K1 | TRIPPING-KED-25-00019 | 0242/20250109/026 | Kedah | Jitra | 11kV | Substation | 09-01-2025 16:34 | PMU BUKIT KAYU HITAM BKH8 | STN SUIS ICQS KJT19258 | PDB KOMP BEBAS CUKAI KJT01109 - PDB RUMAH KELAB BLACKFOREST KJT01110 | Dielectric | Vandalism / Encroachment | RMU SF6 | CABLE | 09-01-2025 17:44 | 09-01-2025 18:28 | 44 | 09-01-2025 18:50 | 13-01-2025 10:10 | 87 | 13-01-2025 11:03 | 90.48 | 1.179g | 1.115g | 1.231g | 1.832g | 1.813g | 2.08g | 1.59 | 1.61 | 1.68
Northern | K1 | TRIPPING-PLS-25-00002 | 2610/20250109/038 | Perlis | Perlis | 11kV | Overhead | 09-01-2025 19:16 | PPU BUKIT KETERI 3K5 | PVCB PANGGAS KAN00281 CB1 | PBT SEMADONG 2 KAN02486 - | Insulation Breakdown | Animal | ABC Conductor | NO FAULT | 09-01-2025 19:19 | 09-01-2025 20:02 | 43 |  |  |  | 09-01-2025 20:10 | 0.9
Northern | K1 | TRIPPING-KED-25-00020 | 0242/20250110/020 | Kedah | Jitra | 11kV | Overhead | 10-01-2025 01:39 | PPU LOJI AIR ARAU GIS 12K5 | PPU LOJI AIR ARAU GIS 12K5 | R/PAM SG PERING KJT19143 - PLB LPN LANA BULU KJT19104 | Insulation Breakdown | Old External Damage | ABC Conductor | CABLE | 10-01-2025 01:41 | 10-01-2025 02:15 | 34 | 10-01-2025 22:11 | 12-01-2025 21:39 | 47 | 12-01-2025 22:52 | 69.22
Northern | K1 | TRIPPING-PLS-25-00003 | 2610/20250110/003 | Perlis | Perlis | 11kV | Underground | 10-01-2025 01:55 | PMU KANGAR CB2 | PMU KANGAR CB2 | PMU KANGAR CB2 - PDB TELEKOM LAMA KANGAR KAN01497 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 10-01-2025 01:59 | 10-01-2025 02:15 | 16 | 20-01-2025 18:49 | 21-01-2025 02:58 | 8 | 21-01-2025 03:13 | 265.3 | 109m | 141m | 128m | 115m | 149m | 134m | 1.05 | 1.05 | 1.04
Northern | K1 | TRIPPING-PLS-25-00004 | 2610/20250110/009 | Perlis | Perlis | 11kV | Underground | 10-01-2025 09:35 | PPU PADANG BESAR CB12 | RPA PADANG BESAR KAN02910 CB1 | CSU BONDED ROAD 2 KAN03319 - CSU BONDED ROAD 1 KAN03234 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 10-01-2025 12:30 | 10-01-2025 13:55 | 85 | 10-01-2025 15:47, 10-01-2025 17:17 | 10-01-2025 16:49, 11-01-2025 23:18 | 1, 30 | 12-01-2025 01:50 | 40.25 | 29.7g | 4.35g | 36.3g | 32.1g | 4.42g | 37g | 1.08 | 1.03 | 1.02
Northern | K1 | TRIPPING-PLS-25-00005 | 2610/20250111/015 | Perlis | Perlis | 11kV | Underground | 11-01-2025 11:00 | PPU PADANG BESAR CB9 | PEKAN KAKI BUKIT KAN00140 CB1 | PAT KG. WANG KELIAN KAN00146 - PDB RPA WANG KELIAN KAN00147 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 11-01-2025 11:07 | 11-01-2025 12:00 | 53 | 13-01-2025 11:42 | 13-01-2025 22:11 | 10 | 13-01-2025 22:33 | 59.55
Northern | K1 | TRIPPING-KED-25-00024 | 0245/20250113/030 | Kedah | Kuala Nerang | 11kV | Overhead | 13-01-2025 20:45 | PPU KUALA NERANG 1K5 | PPU KUALA NERANG 1K5 | PPU KUALA NERANG 1K5 - PBT KUBANG KENDONG 1 KKN00276 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | OVERHEAD LINES | 13-01-2025 20:56 | 13-01-2025 21:02 | 6 | 14-01-2025 17:42 | 16-01-2025 22:55 | 53 | 16-01-2025 23:40 | 74.92 | 345M | 426M | 473M | 528M | 573M | 658M | 1.4 | 1.4 | 1.43
Northern | K1 | TRIPPING-KED-25-00030 | 0242/20250115/024 | Kedah | Jitra | 11kV | Underground | 15-01-2025 15:21 | PPU PELUBANG PL1 | PPU PELUBANG PL1 |  | Open Circuit | Soil Movement | Cable XLPE | NO FAULT | 15-01-2025 15:22 | 15-01-2025 15:58 | 36 | 15-01-2025 17:29 | 15-01-2025 18:48 | 1 | 15-01-2025 18:51 | 3.5
Northern | K1 | TRIPPING-KED-25-00031 | 0242/20250115/026 | Kedah | Jitra | 11kV | Underground | 15-01-2025 16:13 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00742 CB1 | PATOD CHANGKAT NIBONG KJT00739 - PBT KBG BETONG KJT00738 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable PILC | CABLE | 15-01-2025 16:25 | 15-01-2025 16:46 | 21 | 15-01-2025 22:16 | 19-01-2025 20:47 | 94 | 19-01-2025 21:01 | 100.8
Northern | K1 | TRIPPING-KED-25-00034 | 0245/20250117/005 | Kedah | Kuala Nerang | 11kV | Substation | 17-01-2025 14:12 | PPU KUALA NERANG 8K5 | PPU KUALA NERANG 8K5 |  | Possible Animal | NA | None | NO FAULT | 17-01-2025 14:14 | 17-01-2025 14:40 | 26 |  |  |  | 17-01-2025 15:18 | 1.1
Northern | K1 | TRIPPING-KED-25-00036 | 0242/20250118/031 | Kedah | Jitra | 11kV | Underground | 18-01-2025 10:30 | PMU TANJUNG PAUH TP19 | PMU TANJUNG PAUH TP19 | P/P RENCAH NIAGA KJT00382 - PDB SK JITRA 2 KJT00383 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 18-01-2025 10:31 | 18-01-2025 10:46 | 15 |  |  |  | 18-01-2025 21:04 | 10.57
Northern | K1 | TRIPPING-KED-25-00043 | 0242/20250119/028 | Kedah | Jitra | 11kV | Underground | 19-01-2025 12:06 | PPU JERLUN SJ1 | PPU JERLUN SJ1 | PPU JERLUN SJ1 - PLB PEKAN AIR HITAM KJT01419 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 19-01-2025 12:08 | 19-01-2025 12:51 | 43 | 19-01-2025 12:58 | 21-01-2025 22:16 | 57 | 21-01-2025 22:57 | 58.85
Northern | K1 | TRIPPING-PLS-25-00006 | 2610/20250121/029 | Perlis | Perlis | 11kV | Underground | 21-01-2025 16:45 | PMU KANGAR CB6 | PMU KANGAR CB6 | TMN SRI HARTAMAS KAN02903 - VETERINAR KANGAR KAN02974 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 21-01-2025 16:49 | 21-01-2025 17:13 | 24 | 21-01-2025 21:30 | 23-01-2025 23:42 | 50 | 23-01-2025 23:49 | 55.07
Northern | K1 | TRIPPING-PLS-25-00007 | 2610/20250121/066 | Perlis | Perlis | 11kV | Substation | 21-01-2025 23:24 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 |  | Dielectric breakdown | Animal | None | TRANSIENT | 21-01-2025 23:33 | 22-01-2025 00:11 | 38 |  |  |  | 22-01-2025 00:26 | 1.03 | 144M | 134M | 172M | 158M | 145M | 187M | 1.09 | 1.08 | 1.09
Northern | K1 | TRIPPING-PLS-25-00008 | 2610/20250124/020 | Perlis | Perlis | 11kV | Overhead | 24-01-2025 18:22 | PPU PADANG BESAR CB10 | UKK PADANG BESAR KAN00047 | TPK PELUPUSAN SAMPAH RIMBA MAS KAN02824 - PBT CHECK POINT KAN00094 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 24-01-2025 18:45 | 24-01-2025 20:01 | 76 | 02-02-2025 10:50 | 03-02-2025 00:51 | 14 | 03-02-2025 01:05 | 222.72 | 8.7G | 10.6G | 9.3G | 9.4G | 11.5G | 10.5G | 1.08 | 1.08 | 1.1
Northern | K1 | TRIPPING-KED-25-00061 | 0242/20250124/016 | Kedah | Jitra | 11kV | Substation | 24-01-2025 18:29 | PPU KODIANG KD4 | PPU KODIANG KD4 | PPU KODIANG KD4 - PPU LOJI AIR ARAU GIS 14K5 | Dielectric breakdown | Shorted By Animal | None | CABLE | 24-01-2025 18:30 |  | 0 | 24-01-2025 22:13 | 26-01-2025 21:16 | 47 | 26-01-2025 21:14 | 50.75
Northern | K1 | TRIPPING-KED-25-00066 | 0242/20250126/020 | Kedah | Jitra | 11kV | Underground | 26-01-2025 15:06 | PPU JERLUN SJ4 | PDB KLG BERAS SUPREME KJT01676 CB1 |  | Open Circuit | Soil Movement | Cable XLPE | NO FAULT | 26-01-2025 15:07 | 26-01-2025 15:47 | 40 |  |  |  | 26-01-2025 17:30 | 2.4
Northern | K1 | TRIPPING-PLS-25-00010 | 2610/20250128/014 | Perlis | Perlis | 11kV | Overhead | 28-01-2025 10:34 | PMU KANGAR CB6 | PMU KANGAR CB6 | TMN SRI HARTAMAS KAN02903 - VETERINAR KANGAR KAN02974 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 28-01-2025 10:45 | 28-01-2025 10:56 | 11 | 03-02-2025 11:11 | 03-02-2025 23:30 | 12 | 03-02-2025 23:40 | 157.1 | 3.84G | 3.97G | 4.01G | 3.95G | 4.21G | 4.14G | 1.03 | 1.06 | 1.03
Northern | K1 | TRIPPING-KED-25-00072 | 0245/20250128/021 | Kedah | Kuala Nerang | 11kV | Underground | 28-01-2025 13:18 | PPU MINI PPU L/AIR PDG SANAI LA2 | PBT KG. PADANG NYIOR KKN00302 CB1 | PBT KG. PADANG NYIOR KKN00302 - PDB SM PADANG SANAI KKN00304 | Open Circuit | Soil Movement | Cable PILC | CABLE | 28-01-2025 15:20 | 28-01-2025 15:40 | 20 |  |  |  | 30-01-2025 22:25 | 57.12
Northern | K1 | TRIPPING-KED-25-00078 | 0242/20250130/035 | Kedah | Jitra | 11kV | Underground | 30-01-2025 15:27 | PPU PELUBANG PL6 | PPU PELUBANG PL6 | PLB KG. PANCUR KJT00199 - TMN INTAN SHAFINAZ NO.5 KJT19456 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | OVERHEAD LINES | 30-01-2025 15:29 | 30-01-2025 15:55 | 26 | 31-01-2025 00:30 | 01-02-2025 21:04 | 44 | 01-02-2025 21:37 | 54.17 | 104M | 118M | 128M | 123M | 132M | 145M
Northern | K1 | TRIPPING-PLS-25-00011 | 2610/20250130/017 | Perlis | Perlis | 11kV | Underground | 30-01-2025 15:28 | PMU KUALA PERLIS CB12 | PDB DIBUK SYNERGY KAN01260 CB1 | PDB 4 UNIT KLG KAN01275 - PDT KLG TEPONG KAN01272 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 30-01-2025 15:30 | 30-01-2025 16:00 | 30 | 01-02-2025 10:58 | 01-02-2025 22:36 | 11 | 01-02-2025 22:53 | 55.42 | 28.1G | 26.9GG | 25.3G | 31.3G | 29.1G | 27.4G | 1.11 | 1.08 | 1.08
Northern | K1 | TRIPPING-PLS-25-00012 | 2610/20250130/054 | Perlis | Perlis | 11kV | Underground | 30-01-2025 18:33 | PPU SIMPANG EMPAT CB9 | PPU SIMPANG EMPAT CB9 | PDB SK SG. BEREMBANG KAN02303 - PVCB BERNAS PADANG JAMIL KAN01215 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 30-01-2025 18:36 | 30-01-2025 18:50 | 14 | 08-02-2025 11:34 | 08-02-2025 22:50 | 11 | 08-02-2025 23:35 | 221.03 | 2.36G | 150.6M | 3.16G | 2.70G | 161M | 3.32G | 1.14 | 1.07 | 1.05
Northern | K1 | TRIPPING-KED-25-00083 | 0242/20250201/017 | Kedah | Jitra | 11kV | Underground | 01-02-2025 02:00 | PPU CHANGLOON CL4 | PPU CHANGLOON CL4 | TMN JELUTONG FASA 2 KJT19192 - C/SUB TAMAN NAPOH KJT19292 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 01-02-2025 02:03 | 01-02-2025 02:50 | 47 | 01-02-2025 03:29 | 03-02-2025 00:44 | 45 | 03-02-2025 00:57 | 46.95
Northern | K1 | TRIPPING-PLS-25-00013 | 2610/20250201/059 | Perlis | Perlis | 11kV | Underground | 01-02-2025 12:29 | PMU KANGAR CB16 | PMU KANGAR CB16 | PMU KANGAR CB16 - PDB TMN SERI PULAI 3 KAN03053 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 01-02-2025 12:34 | 01-02-2025 13:15 | 41 | 06-03-2025 21:28 | 07-03-2025 17:03 | 19 | 07-03-2025 17:20 | 820.85
Northern | K1 | TRIPPING-PLS-25-00014 | 2610/20250201/068 | Perlis | Perlis | 11kV | Underground | 01-02-2025 12:29 | PMU KANGAR CB1 | PMU KANGAR CB1 | PDB TELEKOM BARU KANGAR KAN00478 - PLB TMN GURU JAYA KAN00477 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 01-02-2025 12:34 | 01-02-2025 13:12 | 38 | 07-02-2025 10:42 | 07-02-2025 22:12 | 11 | 07-02-2025 22:27 | 153.97 | 12.13G | 16.23G | 17.81G | 12.62G | 17.21G | 19.23G | 1.04 | 1.06 | 1.08
Northern | K1 | TRIPPING-KED-25-00084 | 0242/20250201/049 | Kedah | Jitra | 11kV | Underground | 01-02-2025 19:26 | PPU UUM SINTOK ST6 | PDB ASRAMA UUM KJT01743 CB1 | SSD AKADEMI BINAAN MALAYSIA KJT01024 - PDB QTRS UUM SINTOK 1 KJT01025 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 01-02-2025 19:28 | 01-02-2025 20:10 | 42 | 01-02-2025 21:02 | 05-02-2025 19:27 | 94 | 05-02-2025 19:54 | 96.47
Northern | K1 | TRIPPING-KED-25-00086 | 0245/20250202/007 | Kedah | Kuala Nerang | 11kV | Underground | 02-02-2025 16:53 | PPU MINI PPU L/AIR PDG SANAI LA3 | PBT KG. BARU PADANG SANAI KKN00700 CB1 | PBT KG. BARU PADANG SANAI KKN00700 - SMPG EMPAT EMPANGAN AHNING KKN00654 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 02-02-2025 17:40 | 02-02-2025 18:10 | 30 | 04-02-2025 14:30 | 04-02-2025 22:51 | 8 | 04-02-2025 23:11 | 54.3
Northern | K1 | TRIPPING-PLS-25-00015 | 2610/20250202/025 | Perlis | Perlis | 11kV | Underground | 02-02-2025 17:21 | PPU PADANG BESAR CB9 | PVCB TITI TINGGI KAN00091 CB1 | PLB TITI TINGGI ULU KAN01316 - PBT BUKIT CABANG KAN02102 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 02-02-2025 17:24 | 02-02-2025 18:16 | 52 | 04-02-2025 12:58 | 04-02-2025 23:00 | 10 | 04-02-2025 23:06 | 53.75 | 87M | 102M | 131M | 105M | 127M | 159M | 1.21 | 1.24 | 1.21
Northern | K1 | TRIPPING-PLS-25-00016 | 2610/20250203/023 | Perlis | Perlis | 11kV | Overhead | 03-02-2025 16:07 | PMU CHUPING CB3 | PDB UITM ARAU KAN00863 CB1 | PDB KLG BATA-KAN KAN00861 - TMN SISWA KAN02610 | Insulation Breakdown | Animal | ABC Conductor | CABLE | 03-02-2025 16:13 | 03-02-2025 16:40 | 27 | 05-02-2025 10:23 | 06-02-2025 07:31 | 21 | 06-02-2025 08:43 | 64.6 | 236M | 150.6M | 31.6M | 270M | 161M | 33.2M | 1.14 | 1.07 | 1.05
Northern | K1 | TRIPPING-PLS-25-00017 | 2610/20250203/024 | Perlis | Perlis | 11kV | Underground | 03-02-2025 16:07 | PMU CHUPING CB32 | PMU CHUPING TXF32 | CHUPING TX2 - | Insulation Breakdown | Insulation Deterioration | Cable XLPE | TRANSFORMER | 03-02-2025 16:20 |  | 0 | 03-02-2025 19:32 | 05-02-2025 12:00 | 40 | 05-02-2025 12:36 | 44.48 | 372M | 382M | 459M | 483M | 481M | 616M | 1.3 | 1.26 | 1.34
Northern | K1 | TRIPPING-KED-25-00094 | 0242/20250204/024 | Kedah | Jitra | 11kV | Underground | 04-02-2025 14:30 | PPU LOJI AIR ARAU GIS 11K5 | PDB KLG BERAS PERING KJT01776 CB1 |  | Open Circuit | Soil Movement | Cable XLPE | NO FAULT | 04-02-2025 14:35 | 04-02-2025 14:52 | 17 |  |  |  | 04-02-2025 16:08 | 1.63 | 1.764G | 2.45G | 1.99G | 1.782G | 2.58G | 2.01G | 1.01 | 1.05 | 1.01
Northern | K1 | TRIPPING-PLS-25-00018 | 2610/20250211/003 | Perlis | Perlis | 11kV | Underground | 11-02-2025 02:03 | PPU SIMPANG EMPAT CB5 | SEK MEN SANGLANG KAN01095 CB1 | PLB KLG BERAS BAN LEE KAN01128 - PDB K/UDANG RAMADIN KAN01129 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 11-02-2025 02:07 | 11-02-2025 02:45 | 38 | 11-02-2025 23:04 | 16-02-2025 23:05 | 120 | 16-02-2025 23:42 | 141.65 | 410m | 464m | 490m | 636m | 700m | 762m | 1.55 | 1.53 | 1.56
Northern | K1 | TRIPPING-KED-25-00112 | 0242/20250211/012 | Kedah | Jitra | 11kV | Underground | 11-02-2025 10:22 | PPU UUM SINTOK ST5 | PPU UUM SINTOK ST5 | PDB MAKMAL PERINTIS MARDI KJT01059 - PDB BGKL JENTERA KLJ PERTANIAN KJT01737 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 11-02-2025 10:25 | 11-02-2025 11:08 | 43 | 11-02-2025 19:07 | 18-02-2025 23:30 | 172 | 19-02-2025 00:20 | 181.97 | 11.46G | 14.36G | 16.21G | 13.76G | 16.09G | 17.99G | 1.2 | 1.12 | 1.11
Northern | K1 | TRIPPING-PLS-25-00019 | 2610/20250212/017 | Perlis | Perlis | 11kV | Underground | 12-02-2025 09:41 | PMU KANGAR CB2 | PDB TELEKOM LAMA KANGAR KAN00551 CB1 | PDB BANDARAN(NOP) KAN00438 - PDB BUKIT LAGI NO.2 KAN01897 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 12-02-2025 09:48 | 12-02-2025 10:12 | 24 | 19-02-2025 10:56 | 19-02-2025 21:51 | 10 | 19-02-2025 22:25 | 180.73
Northern | K1 | TRIPPING-PLS-25-00020 | 2610/20250212/059 | Perlis | Perlis | 11kV | Underground | 12-02-2025 15:31 | PMU KANGAR CB3 | PDB KOMP KASTAM KANGAR KAN00494 CB1 | PDT TMN CHE YOB KAN03254 - POLIKLINIK BESERI-VVIP KAN00304 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 12-02-2025 15:35 | 12-02-2025 16:02 | 27 | 03-03-2025 17:40 | 07-04-2025 01:08 | 823 | 07-04-2025 01:57 | 1282.43
Northern | K1 | TRIPPING-KED-25-00121 | 0242/20250212/044 | Kedah | Jitra | 11kV | Overhead | 12-02-2025 15:35 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01798 CB1 | PBT KBG BETONG KJT00738 - PATOD CHANGKAT NIBONG KJT00739 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 12-02-2025 16:13 | 12-02-2025 16:40 | 27 | 12-02-2025 17:23 | 20-02-2025 19:09 | 193 | 20-02-2025 20:44 | 197.15
Northern | K1 | TRIPPING-PLS-25-00021 | 2610/20250213/035 | Perlis | Perlis | 11kV | Underground | 13-02-2025 11:54 | PMU KANGAR CB2 | PDB TELEKOM LAMA KANGAR KAN00550 CB1 | PDB KOMP NIAGA BUKIT LAGI KAN00437 - PDB BUKIT LAGI NO.2 KAN01895 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 13-02-2025 11:56 | 13-02-2025 12:39 | 43 | 13-02-2025 16:11 | 13-02-2025 23:24 | 7 | 14-02-2025 00:40 | 12.77
Northern | K1 | TRIPPING-KED-25-00129 | 0245/20250215/001 | Kedah | Kuala Nerang | 11kV | Underground | 15-02-2025 02:28 | PPU KUALA NERANG 5K5 | PDB TMN SRI NERANG KKN00033 CB1 | PDB TMN SRI NERANG KKN00033 - PLB TMN BERSATU-KNRG KKN00035 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 15-02-2025 02:35 | 15-02-2025 04:10 | 95 | 16-02-2025 11:16 | 17-02-2025 05:08 | 17 | 17-02-2025 06:10 | 51.7
Northern | K1 | TRIPPING-KED-25-00130 | 0245/20250215/002 | Kedah | Kuala Nerang | 11kV | Underground | 15-02-2025 02:30 | PPU KUALA NERANG 7K5 | PPU KUALA NERANG 7K5 | PLB BKT TEMBAGA KKN00102 - PLB BUKIT TEMBAGA SELATAN KKN00100 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 15-02-2025 02:35 | 15-02-2025 02:59 | 24 | 15-02-2025 16:31 | 20-02-2025 01:58 | 105 | 20-02-2025 02:08 | 119.63 | 364M | 408M | 368M | 473M | 503M | 516M | 1.39 | 1.37 | 1.4
Northern | K1 | TRIPPING-PLS-25-00022 | 2610/20250217/014 | Perlis | Perlis | 11kV | Underground | 17-02-2025 00:14 | PPU SIMPANG EMPAT CB5 | SEK MEN SANGLANG KAN01095 CB1 | PLB KLG BERAS BAN LEE KAN01128 - PDB K/UDANG RAMADIN KAN01129 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 17-02-2025 00:17 | 17-02-2025 01:02 | 45 | 18-02-2025 23:23 | 25-02-2025 17:25 | 162 | 26-02-2025 17:39 | 233.42 | 136M | 83M | 112M | 142M | 91M | 117M | 40.4 | 57.2 | 47.8
Northern | K1 | TRIPPING-KED-25-00141 | 0242/20250219/024 | Kedah | Jitra | 11kV | Underground | 19-02-2025 11:35 | PMU TANJUNG PAUH TP12 | PMU TANJUNG PAUH TP12 | PDB SUPERMARKET YAWATA KJT00329 - PMU TANJUNG PAUH TP12 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 19-02-2025 11:36 | 19-02-2025 12:05 | 29 | 20-02-2025 10:55 | 23-02-2025 22:41 | 83 | 23-02-2025 23:01 | 107.43 | 24k=80v | 54.8k 132v | brd
Northern | K1 | TRIPPING-PLS-25-00024 | 2610/20250219/005 | Perlis | Perlis | 11kV | Underground | 19-02-2025 14:40 | PPU BUKIT KETERI 3K5 | PPU BUKIT KETERI 3K5B | PAT KG. PADANG JELUTONG - SMK GUAR NANGKA KAN02148 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 19-02-2025 14:42 | 19-02-2025 15:10 | 28 | 01-03-2025 11:16 | 01-03-2025 23:14 | 11 | 01-03-2025 23:26 | 248.77 | 174M | 156M | 191M
Northern | K1 | TRIPPING-KED-25-00150 | 0242/20250222/036 | Kedah | Jitra | 11kV | Underground | 22-02-2025 03:31 | PPU CHANGLOON CL3 | PPU CHANGLOON CL3 | PLB PEKAN CHANGLUN 1 KJT00971 - PDB R/AWAM CHANGLUN KJT00970 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 22-02-2025 03:55 | 22-02-2025 04:38 | 43 | 22-02-2025 21:29 | 24-02-2025 21:42 | 48 | 24-02-2025 22:35 | 67.07
Northern | K1 | TRIPPING-KED-25-00155 | 0242/20250222/136 | Kedah | Jitra | 11kV | Underground | 22-02-2025 19:53 | PPU CHANGLOON CL2 | PPU CHANGLOON CL2 | TMN MERBAU NO 2 KJT19330 - PDB TMN MERANTI-JITRA KJT01629 | Insulation Breakdown | Animal | Cable XLPE | CABLE | 22-02-2025 19:55 | 22-02-2025 21:08 | 73 | 22-02-2025 23:00 | 24-02-2025 22:57 | 47 | 24-02-2025 23:20 | 51.45
Northern | K1 | TRIPPING-KED-25-00164 | 0242/20250225/092 | Kedah | Jitra | 11kV | Underground | 25-02-2025 19:37 | PPU JERLUN SJ6 | PPU JERLUN SJ6 | PBT LUBOK AIR KJT01488 - PBT PERMATANG PAKU KJT01489 | Insulation Breakdown | Animal | Cable XLPE | CABLE | 25-02-2025 19:39 | 25-02-2025 20:00 | 21 | 25-02-2025 20:59, 26-02-2025 21:45 | 25-02-2025 21:47, 01-03-2025 20:59 | 0, 71 | 01-03-2025 22:01 | 98.4 | 395m | 393m | 390m | 639m | 664m | 653m | 1.69 | 1.69 | 1.68
Northern | K1 | TRIPPING-PLS-25-00025 | RE/2610/20250227/PLS/00025 | Perlis | Perlis | 11kV | Underground | 27-02-2025 04:47 | PMU KUALA PERLIS CB13 | PMU KUALA PERLIS CB13 |  |  |  |  | NO FAULT | 27-02-2025 04:56 | 27-02-2025 05:32 | 36 |  |  |  | 03-03-2025 23:40 | 114.88
Northern | K1 | TRIPPING-KED-25-00173 | 0242/20250302/015 | Kedah | Jitra | 11kV | Overhead | 02-03-2025 08:03 | PPU DARULAMAN 9K5 | PPU DARULAMAN 9K5 | PPU DARULAMAN 9K5 - PDB I.L.P KJT01718 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 02-03-2025 08:05 | 02-03-2025 08:35 | 30 | 02-03-2025 09:31 | 03-03-2025 15:27 | 29 | 03-03-2025 15:58 | 31.92 | 139m | 122m | 118m | 153.8m | 132.3m | 127.9m | 1.1 | 1.08 | 1.08
Northern | K1 | TRIPPING-KED-25-00176 | 0242/20250304/064 | Kedah | Jitra | 11kV | Overhead | 04-03-2025 23:27 | PPU DARULAMAN 9K5 | PPU DARULAMAN 9K5 | PLB PUSAT PEMBIAK IKAN KJT00161 - TMN SRI AMAN KJT00162 | Insulation Breakdown | Tree | ABC Conductor | CABLE | 04-03-2025 23:30 | 05-03-2025 00:10 | 40 | 05-03-2025 21:07 | 06-03-2025 12:49 | 15 | 06-03-2025 12:55 | 37.47
Northern | K1 | TRIPPING-KED-25-00178 | 0245/20250305/015 | Kedah | Kuala Nerang | 11kV | Overhead | 05-03-2025 16:08 | PPU MINI PPU L/AIR PDG SANAI LA3 | PPU MINI PPU L/AIR PDG SANAI LA3 | PDB LOJI AIR PADANG SANAI KKN00318 - LDG SG SERAYA KKN00772 | Open Circuit | Soil Movement | ABC Conductor | CABLE | 05-03-2025 16:09 | 05-03-2025 16:25 | 16 | 05-03-2025 22:55 | 07-03-2025 04:09 | 29 | 07-03-2025 04:27 | 36.32
Northern | K1 | TRIPPING-PLS-25-00026 | 2610/20250309/041 | Perlis | Perlis | 11kV | Underground | 09-03-2025 16:36 | PPU SIMPANG EMPAT CB5 | SEK MEN SANGLANG KAN01095 CB1 | PLB KLG BERAS BAN LEE KAN01128 - PDB K/UDANG RAMADIN KAN01129 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 09-03-2025 16:39 | 09-03-2025 17:25 | 46 | 26-03-2025 16:50 | 28-03-2025 09:26 | 40 | 28-03-2025 10:52 | 450.27 | 3.28G | 2.58G | 2.37G | 3.32G | 2.69G | 2.42G | 1.01 | 1.04 | 1.02
Northern | K1 | TRIPPING-KED-25-00186 | 0242/20250312/034 | Kedah | Jitra | 11kV | Overhead | 12-03-2025 08:57 | PMU BUKIT KAYU HITAM BKH5 | BAYAN MAS NO.2 KJT01825 CB1 | PDB BALAI POLIS LAKA TEMIN-NOP KJT01103 - PDB RUMAH KELAB BLACKFOREST KJT19288 | Insulation Breakdown | Tree | ABC Conductor | CABLE | 12-03-2025 09:00 | 12-03-2025 09:42 | 42 | 12-03-2025 21:39 | 14-03-2025 00:25 | 26 | 14-03-2025 01:02 | 40.08
Northern | K1 | TRIPPING-PLS-25-00027 | 2610/20250312/019 | Perlis | Perlis | 11kV | Underground | 12-03-2025 10:30 | PPU PADANG BESAR CB6 | KASTAM UNIT ANJING KAN00071 CB1 | KK3 PADANG BESAR KAN03225 - PBT KEMAJUAN TANAH TITI TINGGI KAN00290 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 12-03-2025 10:33 | 12-03-2025 11:32 | 59 | 12-03-2025 16:47 | 13-03-2025 23:31 | 30 | 13-03-2025 23:41 | 37.18 | 1.571G | 1.292G | 1.338G | 1.603G | 1.331G | 1.379G | 1.02 | 1.03 | 1.03
Northern | K1 | TRIPPING-KED-25-00195 | 0245/20250316/037 | Kedah | Kuala Nerang | 11kV | Overhead | 16-03-2025 00:12 | PPU KUALA NERANG 4K5 | PPU KUALA NERANG 4K5 | PBT KG. SEMELIANG-VVIP KKN00635 - PDB HOSPITAL KUALA NERANG KKN00020 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 16-03-2025 00:21 | 16-03-2025 00:50 | 29 | 16-03-2025 15:35 | 17-03-2025 04:09 | 12 | 17-03-2025 04:17 | 28.08
Northern | K1 | TRIPPING-PLS-25-00029 | 2610/20250316/017 | Perlis | Perlis | 11kV | Underground | 16-03-2025 12:37 | PPU PADANG BESAR CB9 | PEKAN KAKI BUKIT KAN00140 CB1 | PAT KG. WANG KELIAN KAN00146 - PDB RPA WANG KELIAN KAN00147 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 16-03-2025 12:40 | 16-03-2025 13:00 | 20 | 24-03-2025 10:34 | 29-03-2025 00:27 | 109 | 29-03-2025 00:46 | 300.15 | 405M | 438M | 462M | 612M | 653M | 697M | 1.51 | 1.49 | 1.51
Northern | K1 | TRIPPING-PLS-25-00030 | 2610/20250316/038 | Perlis | Perlis | 11kV | Underground | 16-03-2025 17:27 | PMU KANGAR CB16 | SSU GIANT KGAR KAN02771 CB1 | PDT PETRONAS NGV PERLIS KAN02062 - PDB TMN BUDAYA-KAN KAN00587 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 16-03-2025 17:31 | 16-03-2025 17:45 | 14 | 25-03-2025 10:31 | 25-03-2025 23:21 | 12 | 25-03-2025 23:37 | 222.17 | 323M | 246M | 336M | 326M | 256M | 337M | 1.01 | 1.04 | 1
Northern | K1 | TRIPPING-PLS-25-00031 | 2610/20250318/023 | Perlis | Perlis | 11kV | Underground | 18-03-2025 17:06 | PMU BUKIT KETERI SELATAN 9L5 | PPU BUKIT KETERI 1P5 | PPU BUKIT KETERI 1P5 - PPU PADANG BESAR 3L5 | Shorting | Line Sagging / Clearance | Conductor | OVERHEAD LINES | 18-03-2025 17:08 |  | 0 | 22-03-2025 17:26 | 01-05-2025 17:12 | 959 | 01-05-2025 18:11 | 1057.08
Northern | K1 | TRIPPING-KED-25-00205 | 0242/20250319/068 | Kedah | Jitra | 11kV | Underground | 19-03-2025 16:08 | PPU DARULAMAN 9K5 | PPU DARULAMAN 9K5 | PPU DARULAMAN 9K5 - PDB I.L.P KJT01718 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 19-03-2025 16:09 | 19-03-2025 16:28 | 19 | 19-03-2025 17:40 | 22-03-2025 23:12 | 77 | 22-03-2025 23:50 | 79.7 | 307m | 284.4m | 257m | 379m | 291.6m | 285m | 1.24 | 1.04 | 1.22
Northern | K1 | TRIPPING-PLS-25-00032 | 2610/20250324/033 | Perlis | Perlis | 11kV | Overhead | 24-03-2025 12:06 | PMU CHUPING CB6 | FELDA CHUPING NO.2 KAN02699 CB1 | TAMAN FELDA CHUPING 1 KAN02871 - PBT ALFALFA KAN02575 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 24-03-2025 12:20 | 24-03-2025 13:15 | 55 | 28-03-2025 12:09 | 29-03-2025 00:52 | 12 | 29-03-2025 01:55 | 109.82 | 634M | 525M | 887M | 704M | 609M | 1.03G | 1.11 | 1.16 | 1.16
Northern | K1 | TRIPPING-KED-25-00233 | 0242/20250329/012 | Kedah | Jitra | 11kV | Overhead | 29-03-2025 06:01 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00742 CB1 | PBT KBG BETONG - PDB LOJI PENAPIS AIR KJT19342 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 29-03-2025 06:04 | 29-03-2025 06:25 | 21 | 29-03-2025 10:54 | 29-03-2025 21:37 | 10 | 29-03-2025 21:38 | 15.62
Northern | K1 | TRIPPING-PLS-25-00034 | RE/2610/20250329/PLS/00034 | Perlis | Perlis | 11kV | Underground | 29-03-2025 11:49 | PMU KUALA PERLIS CB7 | PDB PANGSAPURI KG.WAI KAN02713 | RE(RSO) REVENUE VANTAGE B - |  |  |  | NO FAULT | 29-03-2025 11:52 | 29-03-2025 12:30 | 38 |  |  |  | 30-03-2025 10:20 | 22.52
Northern | K1 | TRIPPING-KED-25-00238 | 0242/20250403/014 | Kedah | Jitra | 11kV | Underground | 03-04-2025 07:50 | PPU LOJI AIR ARAU GIS 12K5 | PPU LOJI AIR ARAU GIS 12K5 | PLB LPN LANA BULU KJT01312 - PATOD R/PAM MADA MEGAT DEWA KJT18985 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 03-04-2025 07:51 | 03-04-2025 08:21 | 30 | 03-04-2025 21:20 | 05-04-2025 22:08 | 48 | 05-04-2025 22:14 | 62.4
Northern | K1 | TRIPPING-KED-25-00242 | 0242/20250407/056 | Kedah | Jitra | 11kV | Underground | 07-04-2025 23:43 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00742 CB1 | PATOD CHANGKAT NIBONG KJT00739 - PBT KBG BETONG KJT00738 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 08-04-2025 00:00 | 08-04-2025 00:35 | 35 | 08-04-2025 13:52 | 12-04-2025 22:25 | 104 | 12-04-2025 22:32 | 118.82 | 339m | 384m | 428m | 493m | 557m | 630m | 1.45 | 1.45 | 1.48
Northern | K1 | TRIPPING-KED-25-00250 | 0242/20250409/021 | Kedah | Jitra | 11kV | Underground | 09-04-2025 11:29 | PPU JERLUN SJ6 | A/R PIDA 5 | PLB PIDA 3 TUNJANG KJT01519 - SMK PMTG.BONGLAI KJT01518 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 09-04-2025 12:15 | 09-04-2025 12:38 | 23 | 09-04-2025 20:33 | 10-04-2025 21:56 | 25 | 10-04-2025 22:08 | 34.65 | 630m | 651m | 645m | 913m | 952m | 952m | 1.46 | 1.47 | 1.48
Northern | K1 | TRIPPING-KED-25-00253 | 0245/20250410/011 | Kedah | Kuala Nerang | 11kV | Overhead | 10-04-2025 22:42 | PPU KUALA NERANG 10K5 | PPU KUALA NERANG 10K5 | PPU KUALA NERANG 10K5 - PBT KG. PADANG NYIOR KKN00300 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 10-04-2025 22:45 | 10-04-2025 23:18 | 33 | 11-04-2025 15:52 | 13-04-2025 01:52 | 33 | 13-04-2025 17:32 | 66.83 | 302M | 185M | 743M | 308M | 199M | 743M | 16.6 | 26.3 | 6.87
Northern | K1 | TRIPPING-PLS-25-00035 | RE/2610/20250413/PLS/00035 | Perlis | Perlis | 11kV | Underground | 13-04-2025 20:07 | PPU UNIMAP GIS 15K5 | PPU UNIMAP GIS 15K5 | PPU UNIMAP GIS 15K5 - |  |  |  | NO FAULT | 13-04-2025 20:22 | 13-04-2025 20:29 | 7 |  |  |  | 14-04-2025 00:40 | 4.55
Northern | K1 | TRIPPING-PLS-25-00036 | 2610/20250416/009 | Perlis | Perlis | 11kV | Overhead | 16-04-2025 03:14 | PMU KANGAR CB3 | POLIKLINIK BESERI-VVIP KAN00305 CB1 | MEDAN BESERI INDAH KAN02952 - PDB VCB TIMAH TASOH KAN00172 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 16-04-2025 03:17 | 16-04-2025 03:58 | 41 | 16-04-2025 22:54 | 17-04-2025 23:33 | 24 | 18-04-2025 16:16 | 61.03
Northern | K1 | TRIPPING-PLS-25-00037 | 2610/20250419/010 | Perlis | Perlis | 11kV | Underground | 19-04-2025 02:42 | PPU UNIMAP GIS 2K5 | PERLIS PLANTATION KAN00237 CB1 | PBT SG. SERAI KAN00234 - PDT MSM PERLIS KAN03128 | Insulation Breakdown | Improper Installation | Cable XLPE | CABLE | 19-04-2025 02:50 | 19-04-2025 03:30 | 40 | 19-04-2025 11:42 | 20-04-2025 22:53 | 35 | 20-04-2025 23:12 | 44.5 | 1.114G | 849M | 878M | 1.192G | 900M | 887M | 1.07 | 1.06 | 1.01
Northern | K1 | TRIPPING-KED-25-00272 | 0242/20250424/013 | Kedah | Jitra | 11kV | Substation | 24-04-2025 06:11 | PPU JERLUN SJ6 | A/R PIDA 5 | PBT TALIAIR 4 TUNJANG KJT01512 - PAT PIDA 4 TUNJANG KJT01513 | Dielectric breakdown | Bushing Damage | None | CABLE | 24-04-2025 06:45 | 24-04-2025 07:57 | 72 |  |  |  | 24-04-2025 11:12 | 5.02
Northern | K1 | TRIPPING-PLS-25-00038 | 2610/20250426/011 | Perlis | Perlis | 11kV | Substation | 26-04-2025 05:02 | PPU SHORUBBER CB5 | BEHOR MENTALOON KAN00974 CB1 | PAT SEMUT GATAL-VVIP KAN00989 - | Dielectric breakdown | Shorted By Animal | None | NO FAULT | 26-04-2025 05:11 | 26-04-2025 05:36 | 25 |  |  |  | 26-04-2025 06:00 | 0.97
Northern | K1 | TRIPPING-KED-25-00281 | 0242/20250428/002 | Kedah | Jitra | 11kV | Underground | 28-04-2025 06:10 | PPU DARULAMAN 1K5 | TMN NILAM KENCHANA KJT19364 CB1 | PDB MRSM JITRA KJT00953 - PDB PUSAT BELIA JITRA KJT00952 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 28-04-2025 06:13 | 28-04-2025 06:45 | 32 | 29-04-2025 18:00 | 30-04-2025 23:12 | 29 | 30-04-2025 23:40 | 65.5 | 23.0m | 77.0m | 17.50m | 24.4m | 72.7m | 18.49m | 1.07 | 0.94 | 1.06
Northern | K1 | TRIPPING-KED-25-00284 | 0242/20250428/118 | Kedah | Jitra | 11kV | Underground | 28-04-2025 16:38 | PMU TANJUNG PAUH TP6 | BELLEZA GARDEN HOMES KJT18927 CB1 | PDB TMN TABUNG HJ KJT00405 - PDT KG. ALOR RAMBAI KJT19509 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 28-04-2025 16:45 | 28-04-2025 17:15 | 30 | 03-05-2025 21:56 | 04-05-2025 22:47 | 24 | 04-05-2025 23:00 | 150.37 | 601m | 615m | 573m | 727m | 781m | 707m | 1.26 | 1.27 | 1.24
Northern | K1 | TRIPPING-KED-25-00285 | 0242/20250429/019 | Kedah | Jitra | 11kV | Substation | 29-04-2025 01:18 | PPU JERLUN SJ4 | PDB KLG BERAS SUPREME KJT01676 CB1 | PDB SM ALOR BIAK - | Mechanical | Bushing Damage | None | SWITCHGEAR | 29-04-2025 01:23 | 29-04-2025 02:18 | 55 | 02-05-2025 10:49, 03-05-2025 01:35 | 02-05-2025 22:02, 03-05-2025 19:08 | 11, 17 | 03-05-2025 19:30 | 114.2
Northern | K1 | TRIPPING-KED-25-00293 | 0242/20250501/052 | Kedah | Jitra | 11kV | Underground | 01-05-2025 10:40 | PMU TANJUNG PAUH TP14 | PMU TANJUNG PAUH TP14 | PDB TMN MAHSURI FASA 2A KJT00671 - PDB LLM WANG TEPUS KJT00670 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 01-05-2025 10:42 | 01-05-2025 11:10 | 28 | 01-05-2025 14:08 | 03-05-2025 20:54 | 54 | 03-05-2025 21:15 | 58.58
Northern | K1 | TRIPPING-PLS-25-00039 | 2610/20250504/017 | Perlis | Perlis | 11kV | Underground | 04-05-2025 16:35 | PPU PADANG BESAR CB1 | PPU PADANG BESAR CB1 | PPU PADANG BESAR CB1 - PDB B-WAY KAN00058 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 04-05-2025 16:40 | 04-05-2025 16:46 | 6 | 04-05-2025 18:43 | 05-05-2025 09:16 | 14 | 05-05-2025 09:42 | 17.12 | 47.0m | 39.7m | 43.5m | 53.5m | 44.5m | 48.9m | 1.14 | 1.13 | 1.15
Northern | K1 | TRIPPING-PLS-25-00040 | 2610/20250504/053 | Perlis | Perlis | 11kV | Underground | 04-05-2025 19:15 | PPU PADANG BESAR CB12 | SSU MRCB CVIA KAN03298 CB1 | TPK PELUPUSAN SAMPAH RIMBA MAS KAN02824 - PBT CHECK POINT KAN00094, - PBT CHECK POINT KAN00095 - PDB BATU BERTANGKUP KAN00096 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE, CABLE | 04-05-2025 21:00 | 04-05-2025 21:45 | 45 | 05-05-2025 13:55, 05-05-2025 13:57 | 07-05-2025 22:51, 08-05-2025 22:34 | 56, 80 | 08-05-2025 23:45 | 100.5 | 652m | 644m | 609m | 791m | 817m | 757m | 1.27 | 1.27 | 1.25
Northern | K1 | TRIPPING-PLS-25-00042 | 2610/20250508/021 | Perlis | Perlis | 11kV | Underground | 08-05-2025 10:55 | PPU SHORUBBER CB5 | BEHOR MENTALOON KAN00975 CB1 | KLJ KOMUNITI KAN01002 - PLB CEMUMAR TAMBUN TULANG(NOP) KAN01003 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 08-05-2025 11:13 | 08-05-2025 11:24 | 11 | 09-05-2025 00:19 | 10-05-2025 22:30 | 46 | 10-05-2025 22:40 | 59.75
Northern | K1 | TRIPPING-KED-25-00325 | 0242/20250511/068 | Kedah | Jitra | 11kV | Underground | 11-05-2025 20:17 | PPU JERLUN SJ6 | PPU JERLUN SJ6 | PPU JERLUN SJ6 - PATOD AIR HITAM KJT01483 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 11-05-2025 20:29 | 11-05-2025 21:00 | 31 | 12-05-2025 00:49 | 14-05-2025 01:53 | 49 | 14-05-2025 02:27 | 54.17 | 6.09G | 16.93G | 9.66G | 7.46G | 18.02G | 11.47G | 1.23 | 1.06 | 1.2
Northern | K1 | TRIPPING-PLS-25-00043 | 2610/20250513/017 | Perlis | Perlis | 11kV | Substation | 13-05-2025 11:11 | PPU KHEDN 1K5 | ILP BEHOR PULAI KAN00703 CB1 | ILP BEHOR PULAI KAN01564 - | Dielectric breakdown | Bushing Damage | None | TRANSFORMER | 13-05-2025 11:14 | 13-05-2025 11:22 | 8 |  |  |  | 13-05-2025 20:30 | 9.32
Northern | K1 | TRIPPING-KED-25-00326 | 0245/20250513/010 | Kedah | Kuala Nerang | 11kV | Overhead | 13-05-2025 19:03 | PPU KUALA NERANG 7K5 | PPU KUALA NERANG 7K5 | PBT KUALA PAI KJT18890 - SSL KUALA PAI KJT18891 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | OVERHEAD LINES | 13-05-2025 19:30 | 13-05-2025 19:52 | 22 | 14-05-2025 15:15 | 15-05-2025 02:09 | 10 | 15-05-2025 02:18 | 31.25
Northern | K1 | TRIPPING-KED-25-00327 | 0242/20250514/022 | Kedah | Jitra | 11kV | Underground | 14-05-2025 11:04 | PMU TANJUNG PAUH TP6 | BELLEZA GARDEN HOMES KJT18927 CB1 | PDT KG. ALOR RAMBAI KJT19509 - PDB TMN TABUNG HJ KJT00405 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable PILC | CABLE | 14-05-2025 11:00 | 14-05-2025 11:30 | 30 | 14-05-2025 21:19 | 18-05-2025 01:18 | 75 | 18-05-2025 01:26 | 86.37 | 408M | 438M | 410M | 463M | 494M | 454M | 1.13 | 1.13 | 1.11
Northern | K1 | TRIPPING-KED-25-00330 | 0242/20250515/004 | Kedah | Jitra | 11kV | Overhead | 15-05-2025 06:34 | PPU DARULAMAN 4K5 | RUMAH KEDAI 50 UNIT KJT19306 CB1 | RUMAH KEDAI 50 UNIT KJT19306 - TMN SURIA FASA 7 KJT19533 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | OVERHEAD LINES | 15-05-2025 06:43 | 15-05-2025 07:08 | 25 | 15-05-2025 18:55 | 18-05-2025 01:52 | 54 | 18-05-2025 02:01 | 67.45 | 149M | 140M | 156M | 197.2M | 172.6M | 209M | 1.32 | 1.28 | 1.33
Northern | K1 | TRIPPING-KED-25-00332 | RE/0242/20250516/KED/00332 | Kedah | Jitra | 11kV | Underground | 16-05-2025 16:25 | PPU CHANGLOON CL1 | IKS NAPOH KJT19207 CB1 |  |  |  |  | NO FAULT | 16-05-2025 16:26 | 16-05-2025 17:10 | 44 |  |  |  | 17-05-2025 16:26 | 24.02
Northern | K1 | TRIPPING-PLS-25-00046 | 2610/20250517/015 | Perlis | Perlis | 11kV | Underground | 17-05-2025 03:46 | PMU KANGAR CB16 | PMU KANGAR CB16 | PVCB TMN JALI KAN02325 - TMN GUAR SYED ALWI KAN02532 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 17-05-2025 03:49 | 17-05-2025 04:14 | 25 | 17-05-2025 21:10 | 20-05-2025 22:33 | 73 | 20-05-2025 23:10 | 91.4 | 346M | 403M | 442M | 498M | 594M | 649M | 1.45 | 1.47 | 1.5
Northern | K1 | TRIPPING-KED-25-00343 | 0242/20250520/028 | Kedah | Jitra | 11kV | Underground | 20-05-2025 09:27 | PPU CHANGLOON CL3 | PPU CHANGLOON CL3 | PLB PEKAN CHANGLUN 1 KJT00973 - PLB SK YIT MIN KJT00974 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable PILC | CABLE | 20-05-2025 09:34 | 20-05-2025 09:47 | 13 | 24-05-2025 11:36 | 24-05-2025 21:36 | 9 | 24-05-2025 21:46 | 108.32 | 390M | 49.9M | 104M | 393M | 50.0M | 105.5M | 1.01 | 1 | 1
Northern | K1 | TRIPPING-KED-25-00344 | 0242/20250520/029 | Kedah | Jitra | 11kV | Underground | 20-05-2025 09:27 | PPU CHANGLOON CL4 | PPU CHANGLOON CL4 | TMN JELUTONG FASA 2 KJT19192 - C/SUB TAMAN NAPOH KJT19292 | Insulation Breakdown | Soil Movement | Cable XLPE | CABLE | 20-05-2025 09:34 | 20-05-2025 10:00 | 26 | 21-05-2025 21:28 | 24-05-2025 21:51 | 72 | 24-05-2025 22:16 | 108.82 | 699m | 635m | 736m | 844m | 754m | 806m | 1.21 | 1.19 | 1.1
Northern | K1 | TRIPPING-PLS-25-00047 | 2610/20250525/044 | Perlis | Perlis | 11kV | Underground | 25-05-2025 23:13 | PPU KHEDN 3K5 | PPU KHEDN 3K5 | PDB LEBUH RAYA SERIAB KAN00599 - PDB TPAB KAN03286 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 25-05-2025 23:16 | 25-05-2025 23:50 | 34 | 27-05-2025 10:49 | 27-05-2025 22:50 | 12 | 27-05-2025 23:03 | 47.83
Northern | K1 | TRIPPING-PLS-25-00048 | 2610/20250526/048 | Perlis | Perlis | 11kV | Substation | 26-05-2025 15:36 | PMU KUALA PERLIS CB2 | TMN BUNGA PADI KAN00386 CB1 | PDT TMN DESA KATONG KAN00376 - | Insulation Breakdown | Soil Movement | None | SWITCHGEAR | 26-05-2025 15:43 | 26-05-2025 16:05 | 22 | 28-05-2025 11:39 | 29-05-2025 11:03 | 23 | 29-05-2025 11:26 | 67.83 | 2.28G | 2.92G | 1.82G | 3.28G | 3.20G | 1.86G | 1.13 | 1.09 | 1.02
Northern | K1 | TRIPPING-KED-25-00373 | 0242/20250526/102 | Kedah | Jitra | 11kV | Underground | 26-05-2025 20:03 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00742 CB1 | PATOD CHANGKAT NIBONG KJT00739 - PBT KBG BETONG KJT00738 | Dielectric | Dielectric Deterioration | Cable PILC | CABLE | 26-05-2025 20:06 | 26-05-2025 20:19 | 13 | 27-05-2025 22:28 | 29-05-2025 22:19 | 47 | 29-05-2025 22:40 | 74.62 | 98.2M | 93.5M | 96.4M | 120.9M | 114M | 116M | 1.11 | 1.09 | 1.09
Northern | K1 | TRIPPING-PLS-25-00049 | 2610/20250530/003 | Perlis | Perlis | 11kV | Overhead | 30-05-2025 07:51 | PPU PADANG BESAR CB9 | PPU PADANG BESAR CB9 | PPU PADANG BESAR CB9 - PVCB TITI TINGGI KAN00090 | Dielectric | Moisture | ABC Conductor | CABLE | 30-05-2025 07:54 |  | 0 | 30-05-2025 08:57 | 30-05-2025 09:05 | 0 | 30-05-2025 09:20 | 1.48
Northern | K1 | TRIPPING-KED-25-00385 | 0242/20250601/003 | Kedah | Jitra | 11kV | Substation | 01-06-2025 09:21 | PPU JERLUN SJ6 | A/R PIDA 5 |  | Open Circuit | Soil Movement | None | SWITCHGEAR | 01-06-2025 09:50 | 01-06-2025 10:13 | 23 | 05-06-2025 21:34 | 06-06-2025 15:48 | 18 | 06-06-2025 17:08 | 127.78 | 93.4m | 110.1m | 108.0m | 101.4m | 113.5m | 112.8m | 1.09 | 1.04 | 1.04
Northern | K1 | TRIPPING-KED-25-00387 | 0242/20250601/034 | Kedah | Jitra | 11kV | Overhead | 01-06-2025 10:21 | PPU JERLUN SJ2 | SS 11KV SAMAK KJT19322 | SS 11KV SAMAK KJT19322 - PDB KLG PROSES UDANG KERPAN KJT01687 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 01-06-2025 11:23 | 01-06-2025 11:49 | 26 | 01-06-2025 22:31 | 03-06-2025 19:08 | 44 | 03-06-2025 20:00 | 57.65
Northern | K1 | TRIPPING-KED-25-00389 | 0245/20250602/002 | Kedah | Kuala Nerang | 11kV | Underground | 02-06-2025 08:15 | PPU KUALA NERANG 7K5 | PBT PONG MANIS KKN00171 CB1 |  |  |  |  | NO FAULT | 02-06-2025 09:45 | 02-06-2025 10:12 | 27 |  |  |  | 02-06-2025 10:42 | 2.45
Northern | K1 | TRIPPING-KED-25-00390 | 0242/20250602/021 | Kedah | Jitra | 11kV | Underground | 02-06-2025 11:16 | PPU DARULAMAN 6K5 | PPU DARULAMAN 6K5 | PPU DARULAMAN 6K5 - SEKOLAH MEN SERI MAHAWANGSA KJT19070 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 02-06-2025 11:17 | 02-06-2025 11:40 | 23 | 04-06-2025 10:38 | 04-06-2025 21:16 | 10 | 05-06-2025 22:25 | 83.15 | 666M | 688M | 642M | 932M | 869M | 791M | 1.26 | 1.27 | 1.24
Northern | K1 | TRIPPING-PLS-25-00052 | RE/2610/20250603/PLS/00052 | Perlis | Perlis | 11kV | Underground | 03-06-2025 10:36 | PPU UNIMAP GIS 1K5 | SSD UNIMAP ULU PAUH KAN02786 |  |  |  |  | NO FAULT | 03-06-2025 21:03 | 03-06-2025 22:54 | 111 |  |  |  | 04-06-2025 18:33 | 31.95
Northern | K1 | TRIPPING-PLS-25-00053 | 2610/20250604/020 | Perlis | Perlis | 11kV | Overhead | 04-06-2025 15:07 | PMU KANGAR CB16 | PVCB TMN JALI KAN02326 CB1 |  | Insulation Breakdown | Animal | ABC Conductor | NO FAULT | 04-06-2025 15:10 | 04-06-2025 15:28 | 18 |  |  |  | 04-06-2025 16:33 | 1.43
Northern | K1 | TRIPPING-PLS-25-00054 | 2610/20250606/021 | Perlis | Perlis | 11kV | Underground | 06-06-2025 15:05 | PMU CHUPING CB6 | FELDA CHUPING NO.2 KAN02699 CB1 | FELDA CHUPING NO.2 KAN02699 - PDB FELDA CHUPING 4 KAN02573 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 06-06-2025 15:08 | 06-06-2025 16:00 | 52 | 09-06-2025 10:52 | 09-06-2025 22:46 | 11 | 09-06-2025 22:59 | 79.9 | 295M | 427M | 201M | 321M | 495M | 216M | 1.1 | 1.16 | 1.06
Northern | K1 | TRIPPING-PLS-25-00055 | 2610/20250606/063 | Perlis | Perlis | 11kV | Underground | 06-06-2025 23:04 | PPU SIMPANG EMPAT CB7 | PPU SIMPANG EMPAT CB7 | SK SG. BARU KAN02334 - PDB LOJI AIR SG. BARU KAN01141 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 06-06-2025 23:09 |  | 0 | 07-06-2025 22:16, 11-06-2025 09:30 | 11-06-2025 09:23, 12-06-2025 08:35 | 83, 23 | 12-06-2025 08:46 | 129.7 | 1.359G | 1.366G | 1.409G | 2.22G | 2.21G | 2.26G | 1.65 | 1.61 | 1.61
Northern | K1 | TRIPPING-KED-25-00404 | 0242/20250608/026 | Kedah | Jitra | 11kV | Underground | 08-06-2025 19:08 | PMU TANJUNG PAUH TP18 | S/SUIS INTRA GROWTH KJT18946 | SSD INST.LAT.PERINDUSTRIAN-ILP KJT00139 - TMN SRI AMAN KJT00140 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 08-06-2025 20:55 | 08-06-2025 21:15 | 20 | 09-06-2025 21:21 | 11-06-2025 22:28 | 49 | 11-06-2025 22:35 | 75.45 | 50.2m | 56.5m | 67.4m | 59.0m | 77.9m | 86.1m | 1.19 | 1.22 | 1.27
Northern | K1 | TRIPPING-KED-25-00405 | 0242/20250609/005 | Kedah | Jitra | 11kV | Overhead | 09-06-2025 03:43 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01800 CB1 | PDB SAFETY GLASS KJT00752 - PDB TMN SINAR HARAPAN KJT00753 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 09-06-2025 03:45 | 09-06-2025 04:10 | 25 | 09-06-2025 21:18 | 10-06-2025 22:24 | 25 | 10-06-2025 22:25 | 42.7 | 138.4M | 118.8M | 133.2M | 154.1M | 128.5M | 145.5M | 1.11 | 1.08 | 1.09
Northern | K1 | TRIPPING-KED-25-00423 | 0242/20250616/006 | Kedah | Jitra | 11kV | Underground | 16-06-2025 12:11 | PPU PELUBANG PL5 | PPU PELUBANG PL5 | PDB TMN MELOR 2 KJT00663 - PDB APARTMENT 8 TINGKAT KJT00662 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 16-06-2025 12:13 | 16-06-2025 12:31 | 18 | 16-06-2025 23:29 | 19-06-2025 23:19 | 71 | 20-06-2025 23:15 | 107.07 | 123.8M | 103.2M | 142.9M | 150.5M | 120.3M | 178M | 1.22 | 1.17 | 1.25
Northern | K1 | TRIPPING-KED-25-00426 | 0242/20250617/043 | Kedah | Jitra | 11kV | Underground | 17-06-2025 20:51 | PPU KODIANG KD6 | PPU KODIANG KD6 | PLB PEKAN KODIANG KJT01235 - PLB LPN KODIANG KJT01364 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 17-06-2025 21:03 | 17-06-2025 21:35 | 32 | 18-06-2025 15:42 | 18-06-2025 22:43 | 7 | 18-06-2025 22:48 | 25.95 | 5.92G | 7.10G | 7.03G | 6.05G | 7.14G | 7.10G | 1.02 | 1 | 1
Northern | K1 | TRIPPING-KED-25-00429 | 0242/20250618/032 | Kedah | Jitra | 11kV | Underground | 18-06-2025 14:15 | PMU TANJUNG PAUH TP6 | BELLEZA GARDEN HOMES KJT18927 CB1 | PDT KG. ALOR RAMBAI KJT19509 - PDB TMN TABUNG HJ KJT00405 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 18-06-2025 14:18 | 18-06-2025 14:38 | 20 | 18-06-2025 23:00 | 21-06-2025 22:57 | 71 | 21-06-2025 23:11 | 80.93 | 3.39G | 5.72G | 2.73G | 3.93G | 5.67G | 2.61G | 1.16 | 1 | 1
Northern | K1 | TRIPPING-KED-25-00436 | 0242/20250623/007 | Kedah | Jitra | 11kV | Overhead | 23-06-2025 09:20 | PPU KODIANG KD1 | SSBT RUMAH PAM PERING KJT01634 | PAT CEROK MOKAM 2 KJT01220 - PADAT YUNG HENG POULTRY 2 KJT19453 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 23-06-2025 09:32 | 23-06-2025 10:08 | 36 | 23-06-2025 21:03 | 25-06-2025 21:27 | 48 | 25-06-2025 22:01 | 60.68
Northern | K1 | TRIPPING-KED-25-00443 | 0242/20250625/077 | Kedah | Jitra | 11kV | Underground | 25-06-2025 16:06 | PMU TANJUNG PAUH TP20 | PMU TANJUNG PAUH TP20 | PDB SK JITRA 2 KJT00004 - PLB TMN KENANGA-JITRA KJT00003 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 25-06-2025 16:09 | 25-06-2025 16:40 | 31 | 25-06-2025 22:17 | 29-06-2025 02:20 | 76 | 29-06-2025 03:05 | 82.98 | 687M | 649M | 630M | 942M | 931M | 909M | 1.39 | 1.46 | 1.46
Northern | K1 | TRIPPING-KED-25-00444 | 0242/20250626/009 | Kedah | Jitra | 11kV | Underground | 26-06-2025 10:02 | PMU TANJUNG PAUH TP6 | BELLEZA GARDEN HOMES KJT18927 CB1 | PBT ALOR RAMBAI-JITRA KJT00404 - PDT KG. ALOR RAMBAI KJT19508 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable PILC | CABLE | 26-06-2025 10:26 | 26-06-2025 10:49 | 23 | 26-06-2025 22:40 | 29-06-2025 19:19 | 68 | 29-06-2025 19:31 | 81.48 | 14.11G | 22.1G | 15.79G | 16.64G | 24.6G | 18.77G | 1.2 | 1.15 | 1.19
Northern | K1 | TRIPPING-KED-25-00445 | 0242/20250626/044 | Kedah | Jitra | 11kV | Underground | 26-06-2025 13:29 | PMU TANJUNG PAUH TP14 | PMU TANJUNG PAUH TP14 | PDB BANGLO NO.1 KJT00198 - PDB QTRS PELUBANG KJT00202 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable PILC | CABLE | 26-06-2025 13:41 | 26-06-2025 14:02 | 21 | 26-06-2025 22:41, 29-06-2025 10:46, 11-07-2025 22:36 | 28-06-2025 11:28, 11-07-2025 20:46, 17-07-2025 21:14 | 36, 297, 142 | 17-07-2025 21:30 | 512.02
Northern | K1 | TRIPPING-KED-25-00446 | 0242/20250626/082 | Kedah | Jitra | 11kV | Underground | 26-06-2025 18:35 | PPU JERLUN SJ4 | PDB KLG BERAS SUPREME KJT01676 CB1 | PDB SM ALOR BIAK KJT01553 - PAT KOTA RENTANG KJT01554 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 26-06-2025 18:40 | 26-06-2025 19:10 | 30 | 28-06-2025 11:37 | 28-06-2025 22:46 | 11 | 29-06-2025 00:25 | 53.83
Northern | K1 | TRIPPING-PLS-25-00056 | 2610/20250627/043 | Perlis | Perlis | 11kV | Underground | 27-06-2025 14:32 | PPU SHORUBBER CB11 | PDB RPA JEJAWI KAN00758 | PDB TMN GEMBIRA-KAN KAN02234 - PVCB REPOH CERIA-VVIP KAN02631 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 27-06-2025 14:35 | 27-06-2025 14:44 | 9 | 28-06-2025 10:45 | 28-06-2025 22:02 | 11 | 28-06-2025 22:10 | 31.63 | 116.2M | 87.0M | 105.7M | 139.5M | 100.0M | 128.2M | 1.21 | 1.15 | 1.22
Northern | K1 | TRIPPING-KED-25-00457 | 0245/20250629/044 | Kedah | Kuala Nerang | 11kV | Underground | 29-06-2025 18:57 | PPU NAKA 6K5 | PPU NAKA 6K5 | PDB PERUMAHAN LDG SG TEKAI KKN00642 - PBT KG. PADANG-K.NERANG KKN00435 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 29-06-2025 18:59 | 29-06-2025 19:34 | 35 | 01-07-2025 11:59 | 02-07-2025 01:53 | 13 | 02-07-2025 03:06 | 56.15 | 15.85G | 18.28G | 13.26G | 19.00G | 20.4G | 15.44G | 1.2 | 1.12 | 1.16
Northern | K1 | TRIPPING-KED-25-00461 | 0242/20250702/024 | Kedah | Jitra | 11kV | Underground | 02-07-2025 11:03 | PMU TANJUNG PAUH TP6 | BELLEZA GARDEN HOMES KJT18927 CB1 | PBT ALOR RAMBAI-ALS KJT00401 - PBT ALOR RAMBAI-JITRA KJT00402 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 02-07-2025 11:06 | 02-07-2025 12:01 | 55 | 12-07-2025 11:11, 12-07-2025 13:19 | 12-07-2025 17:59, 12-07-2025 13:40 | 6, 0 | 12-07-2025 18:17 | 247.23 | 480m | 405m | 0 | 515m | 494m |  | 1.08 | 1.22
Northern | K1 | TRIPPING-KED-25-00462 | 0242/20250702/039 | Kedah | Jitra | 11kV | Overhead | 02-07-2025 11:25 | PPU PELUBANG PL3 | PPU PELUBANG PL3 | PPU PELUBANG PL3 - PBT KOTA MENGKUANG KJT00686 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 02-07-2025 11:27 | 02-07-2025 11:50 | 23 | 02-07-2025 22:13 | 05-07-2025 21:48 | 71 | 05-07-2025 22:20 | 82.92 | 148.5M | 149.4M | 148.4M | 167.1M | 167.0M | 164.5M | 1.13 | 1.12 | 1.11
Northern | K1 | TRIPPING-PLS-25-00060 | 2610/20250712/028 | Perlis | Perlis | 11kV | Overhead | 12-07-2025 11:40 | PMU KANGAR CB16 | PVCB TMN JALI KAN02326 CB1 | PBT BUKIT KAYA KAN00563 - C/SUB SK SRI PERLIS KAN02279 | Insulation Breakdown | Animal | ABC Conductor | CABLE | 12-07-2025 11:44 | 12-07-2025 12:10 | 26 | 12-07-2025 22:35, 13-07-2025 11:27 | 13-07-2025 10:08, 13-07-2025 21:21 | 11, 9 | 13-07-2025 21:58 | 34.3 | 61.2M | 145.5M | 658M | 71.1MM | 158.6M | 694M | 1.13 | 1.09 | 1.06
Northern | K1 | TRIPPING-KED-25-00502 | 0242/20250719/015 | Kedah | Jitra | 11kV | Underground | 19-07-2025 11:43 | PPU JERLUN SJ6 | A/R PIDA 5 | SMK PMTG.BONGLAI KJT01518 - PLB PIDA 3 TUNJANG KJT01519 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 19-07-2025 12:05 | 19-07-2025 12:47 | 42 | 19-07-2025 15:17, 21-07-2025 22:56 | 21-07-2025 22:55, 22-07-2025 21:40 | 55, 22 | 22-07-2025 22:10 | 82.45 | 645M | 238M | 693M | 981M | 265M | 1.015G | 1.51 | 1.12 | 1.47
Northern | K1 | TRIPPING-PLS-25-00061 | 2610/20250720/082 | Perlis | Perlis | 11kV | Underground | 20-07-2025 18:06 | PMU KUALA PERLIS CB7 | PDB PANGSAPURI KG.WAI KAN00647 CB1 | PLB RPA BUKIT KUBU KAN00635 - PDB PELADANG JAYA KAN00651 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 20-07-2025 18:16 | 20-07-2025 18:30 | 14 | 21-07-2025 01:24, 24-07-2025 21:47 | 23-07-2025 23:02, 26-07-2025 23:22 | 69, 49 | 26-07-2025 23:37 | 149.52 | 1.600G | 1.711G | 1.724G | 2.59G | 2.72G | 2.73G | 1.62 | 1.6 | 1.61
Northern | K1 | TRIPPING-KED-25-00505 | 0242/20250720/065 | Kedah | Jitra | 11kV | Overhead | 20-07-2025 18:10 | PPU DARULAMAN 9K5 | PPU DARULAMAN 9K5 | PLB PUSAT PEMBIAK IKAN KJT00161 - TMN SRI AMAN KJT00162 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 20-07-2025 18:17 | 20-07-2025 18:35 | 18 | 21-07-2025 22:05 | 23-07-2025 20:57 | 46 | 23-07-2025 21:20 | 75.17
Northern | K1 | TRIPPING-KED-25-00524 | RE/0242/20250725/KED/00524 | Kedah | Jitra | 11kV | Underground | 25-07-2025 18:41 | PPU CHANGLOON CL1 | IKS NAPOH KJT19207 CB1 |  |  |  |  | NO FAULT | 25-07-2025 18:55 |  | 0 | 26-07-2025 15:16 | 29-07-2025 17:50 | 74 | 29-07-2025 18:10 | 95.48
Northern | K1 | TRIPPING-PLS-25-00062 | 2610/20250728/011 | Perlis | Perlis | 11kV | Underground | 28-07-2025 04:18 | PMU KANGAR CB4 | PMU KANGAR CB4 | PDB PERLIS TEACHING SCHOOL KAN02001 - PDB MKTB PERGURUAN 2-KAN KAN00708 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 28-07-2025 04:21 | 28-07-2025 04:56 | 35 | 30-07-2025 00:33 | 31-07-2025 00:56 | 24 | 31-07-2025 01:07 | 68.82 | 354M | 437M | 400M | 418M | 539M | 482M | 1.18 | 1.24 | 1.2
Northern | K1 | TRIPPING-PLS-25-00064 | 2610/20250729/012 | Perlis | Perlis | 11kV | Underground | 29-07-2025 04:41 | PMU KANGAR CB10 | PDB FLAT POLIS KANGAR KAN00517 | PDB FLAT POLIS KANGAR KAN00517 - PDB HOSPITAL BARU KANGAR KAN00499 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 29-07-2025 05:28 | 29-07-2025 05:58 | 30 | 09-08-2025 10:43 | 09-08-2025 21:38 | 10 | 09-08-2025 22:08 | 281.45 | 128.4M | 128M | 147M | 153.7M | 125.5M | 182.8M | 1.22 | 1.17 | 1.21
Northern | K1 | TRIPPING-PLS-25-00063 | 2610/20250729/011 | Perlis | Perlis | 11kV | Underground | 29-07-2025 05:17 | PMU KANGAR CB2 | PDB TELEKOM LAMA KANGAR KAN00551 CB1 | PDB BILIK SEJUK FAMA KAN00428 - PDB R/KDAI PENGKALAN ASAM KAN00427 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 29-07-2025 05:23 | 29-07-2025 05:47 | 24 | 01-08-2025 09:56 | 01-08-2025 23:28 | 13 | 01-08-2025 23:50 | 90.55
Northern | K1 | TRIPPING-PLS-25-00065 | 2610/20250731/068 | Perlis | Perlis | 11kV | Underground | 31-07-2025 21:44 | PPU SHORUBBER CB7 | PDB TMN HARMONI KANGAR KAN01924 | PDB PUTRA PALACE B KAN00508 - PDB SPG TIGA (SPG3) KAN00720 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 31-07-2025 21:50 | 31-07-2025 22:03 | 13 | 05-08-2025 22:52, 10-08-2025 10:37 | 10-08-2025 23:24, 10-08-2025 23:21 | 120, 12 | 10-08-2025 23:36 | 241.87 | 93.7M | 106.2M | 119.1M | 102.9M | 117.7M | 137.7M | 1.1 | 1.11 | 1.16
Northern | K1 | TRIPPING-PLS-25-00066 | 2610/20250802/011 | Perlis | Perlis | 11kV | Underground | 02-08-2025 09:34 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 | PDB JPJ JEJAWI KAN00748 - PDB SEDC TMN JEJAWI-VVIP KAN00749 | Insulation Breakdown | Animal | Cable XLPE | CABLE | 02-08-2025 09:36 | 02-08-2025 09:58 | 22 | 02-08-2025 22:18, 05-08-2025 22:24 | 05-08-2025 22:20, 06-08-2025 01:12 | 72, 2 | 06-08-2025 01:26 | 87.87 | 335M | 336M | 386M | 435M | 432M | 515M | 1.31 | 1.29 | 1.34
Northern | K1 | TRIPPING-PLS-25-00067 | 2610/20250803/017 | Perlis | Perlis | 11kV | Overhead | 03-08-2025 10:10 | PPU POLITEKNIK PAUH PERLIS 2 | PPU POLITEKNIK PAUH PERLIS CB2 | L/S FELCRA ULU PAUH KAN00892 - TMN INDUSTRI PAUH KAN02497 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 03-08-2025 10:13 | 03-08-2025 10:47 | 34 | 05-08-2025 11:18 | 06-08-2025 00:22 | 13 | 06-08-2025 01:32 | 63.37 | 418M | 435M | 443M | 567M | 593M | 608M | 1.36 | 1.36 | 1.37
Northern | K1 | TRIPPING-PLS-25-00068 | 2610/20250806/039 | Perlis | Perlis | 11kV | Underground | 06-08-2025 11:41 | PPU SHORUBBER CB8 | PDB TMN HARMONI KANGAR KAN01925 CB1 | PDB I/PEJ BOMBA KANGAR KAN02039 - PDB KOMP KASTAM KANGAR KAN00497 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 06-08-2025 11:44 | 06-08-2025 12:15 | 31 | 07-08-2025 00:16, 11-08-2025 10:15 | 07-08-2025 02:42, 11-08-2025 22:34, 11-08-2025 22:08 | 2, 11 | 11-08-2025 22:29 | 130.8
Northern | K1 | TRIPPING-KED-25-00550 | 0245/20250807/009 | Kedah | Kuala Nerang | 11kV | Underground | 07-08-2025 05:50 | PPU NAKA 6K5 | PPU NAKA 6K5 | PDB PERUMAHAN LDG SG TEKAI KKN00642 - PBT KG. PADANG-K.NERANG KKN00435 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 07-08-2025 05:54 | 07-08-2025 06:37 | 43 | 07-08-2025 15:33 | 10-08-2025 22:22 | 78 | 10-08-2025 23:11 | 89.35 | 15.85G | 13.3G | 13.33G | 18.92G | 15.20G | 13.60G | 1.19 | 1.15 | 1.11
Northern | K1 | TRIPPING-PLS-25-00069 | RE/2610/20250810/PLS/00069 | Perlis | Perlis | 11kV | Underground | 10-08-2025 12:31 | PPU UNIMAP GIS 1K5 | SSD UNIMAP ULU PAUH KAN02786 |  |  |  |  | NO FAULT | 10-08-2025 12:35 | 10-08-2025 13:02 | 27 |  |  |  | 10-08-2025 22:15 | 9.73
Northern | K1 | TRIPPING-KED-25-00565 | 0242/20250812/009 | Kedah | Jitra | 11kV | Underground | 12-08-2025 13:34 | PMU BUKIT KAYU HITAM BKH9 | STN SUIS ICQS KJT19258 CB1 | PLUS BKH KJT19275 - KEM KAWALAN SEMPADAN KJT19551 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 12-08-2025 13:37 | 12-08-2025 13:52 | 15 | 12-08-2025 22:55, 31-08-2025 10:41 | 21-08-2025 10:51, 01-09-2025 22:07 | 203, 35 | 01-09-2025 22:18 | 488.73 | 158.2M | 235M | 190.2M | 186.4M | 301M | 195.1M | 1.18 | 1.28 | 1.01
Northern | K1 | TRIPPING-PLS-25-00071 | 2610/20250812/207 | Perlis | Perlis | 11kV | Underground | 12-08-2025 21:56 | PMU KUALA PERLIS CB1 | PDB AMAN FISHMEAL KAN00623 CB1 | PAT SS BANGSAL LEBAH KAN00619 - PBT TOK KUNING 2 KAN00618 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 12-08-2025 21:58 | 12-08-2025 22:10 | 12 | 13-08-2025 17:20 | 18-08-2025 22:18 | 124 | 18-08-2025 22:45 | 144.82 | 138.6M | 138.1M | 139.2M | 143.2M | 140.3M | 141.3M | 1.03 | 1.12 | 1.13
Northern | K1 | TRIPPING-PLS-25-00072 | 2610/20250814/002 | Perlis | Perlis | 11kV | Overhead | 14-08-2025 00:19 | PPU UNIMAP GIS 2K5 | FELDA CHUPING NO.2 KAN02702 CB1 |  | Insulation Breakdown | Animal | ABC Conductor | NO FAULT | 14-08-2025 00:29 | 14-08-2025 01:00 | 31 |  |  |  | 14-08-2025 01:34 | 1.25
Northern | K1 | TRIPPING-KED-25-00568 | RE/0242/20250814/KED/00568 | Kedah | Jitra | 11kV | Underground | 14-08-2025 03:12 | PPU CHANGLOON CL1 | IKS NAPOH KJT19207 | RE(KSO) DEKAD ALIRAN SURIA B - |  |  |  | CABLE | 14-08-2025 03:25 |  | 0 | 15-08-2025 10:23 | 15-08-2025 16:32, 15-08-2025 16:34 | 6 | 15-08-2025 16:40 | 37.47
Northern | K1 | TRIPPING-KED-25-00569 | 0242/20250814/034 | Kedah | Jitra | 11kV | Underground | 14-08-2025 15:19 | PMU BUKIT KAYU HITAM BKH3 | PMU BUKIT KAYU HITAM BKH3 | PMU BUKIT KAYU HITAM BKH3 - PDB STONE SEAL KJT01112 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 14-08-2025 15:22 | 14-08-2025 15:50 | 28 | 14-08-2025 23:09 | 23-08-2025 19:27 | 212 | 23-08-2025 20:38 | 221.32 | 176.7M | 245M | 207M | 191.4M | 270M | 226M | 1.08 | 1.1 | 1.09
Northern | K1 | TRIPPING-KED-25-00570 | 0245/20250814/006 | Kedah | Kuala Nerang | 11kV | Underground | 14-08-2025 16:29 | PPU MINI PPU L/AIR PDG SANAI LA3 | PPU MINI PPU L/AIR PDG SANAI LA3 | PDB LOJI AIR PADANG SANAI KKN00318 - LDG SG SERAYA KKN00772 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 14-08-2025 16:32 | 14-08-2025 17:00 | 28 | 14-08-2025 22:14 | 15-08-2025 23:20 | 25 | 16-08-2025 00:34 | 32.08
Northern | K1 | TRIPPING-KED-25-00571 | 0242/20250814/064 | Kedah | Jitra | 11kV | Overhead | 14-08-2025 16:30 | PMU BUKIT KAYU HITAM BKH10 | PLB SMPG BKT.TANGGA KJT00877 CB1 | PDT SEMARAK API NO.3 KJT19400 - TMN SEMARAK API NO 2 KJT19126 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 14-08-2025 17:00 | 14-08-2025 17:20 | 20 | 16-08-2025 10:34 | 16-08-2025 22:36 | 12 | 16-08-2025 22:40 | 54.17
Northern | K1 | TRIPPING-KED-25-00577 | 0245/20250816/025 | Kedah | Kuala Nerang | 11kV | Underground | 16-08-2025 22:14 | PPU NAKA 6K5 | PBT KG. PADANG-K.NERANG KKN00437 CB1 | PBT KG. PADANG-K.NERANG KKN00437 - PATOD SG. LONG KKN00439 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 16-08-2025 23:11 | 16-08-2025 23:45 | 34 | 17-08-2025 12:18 | 21-08-2025 01:23 | 85 | 21-08-2025 01:43 | 99.48
Northern | K1 | TRIPPING-KED-25-00581 | 0242/20250818/094 | Kedah | Jitra | 11kV | Underground | 18-08-2025 23:42 | PMU TANJUNG PAUH TP15 | PMU TANJUNG PAUH TP15 | PMU TANJUNG PAUH TP15 - PDB KAWAN SUPERMARKET KJT00415 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 18-08-2025 23:46 | 19-08-2025 00:20 | 34 | 19-08-2025 22:41 | 03-09-2025 22:14 | 359 | 04-09-2025 21:48 | 406.1 | 96.7M | 95.0M | 99.2M | 102.3M | 101.8M | 105.0M | 1.06 | 1.03 | 1.06
Northern | K1 | TRIPPING-KED-25-00591 | 0245/20250823/008 | Kedah | Kuala Nerang | 11kV | Underground | 23-08-2025 11:37 | PPU NAKA 6K5 | PPU NAKA 6K5 | PBT KG. CHANDING KKN00419 - PLT SK LAMDIN KKN00421 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 23-08-2025 11:42 | 23-08-2025 12:25 | 43 | 23-08-2025 22:24 | 27-08-2025 18:29 | 92 | 27-08-2025 20:17 | 104.67 | 214M | 190M | 160M | 243M | 204M | 296M | 1.15 | 1.07 | 1.36
Northern | K1 | TRIPPING-PLS-25-00073 | 2610/20250823/020 | Perlis | Perlis | 11kV | Substation | 23-08-2025 11:54 | PMU CHUPING CB8 | TAE HWA KAN00225 CB1 | PDB SEK.DATO JAAFAR HASSAN KAN01359 - | Dielectric breakdown | Insulation Deterioration | None | TRANSFORMER | 23-08-2025 11:57 | 23-08-2025 12:18 | 21 | 26-08-2025 10:38 | 26-08-2025 22:02 | 11 | 26-08-2025 22:43 | 82.82 | 597M | 617M | 938M | 678M | 692M | 1.214G | 1.14 | 1.12 | 1.31
Northern | K1 | TRIPPING-KED-25-00596 | 0242/20250824/193 | Kedah | Jitra | 11kV | Underground | 24-08-2025 20:24 | PPU CHANGLOON CL6 | PPU CHANGLOON CL6 | PDB TELEKOM CHANGLUN KJT00893 - SEK MEN CHANGLUN KJT00892 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 24-08-2025 20:26 | 24-08-2025 21:00 | 34 | 25-08-2025 22:35 | 02-09-2025 21:56 | 191 | 02-09-2025 22:07 | 217.72 | 178.1M | 142.2M | 161.2M | 187.9M | 147.9M | 164.5M | 1.06 | 1.03 | 1.01
Northern | K1 | TRIPPING-PLS-25-00074 | 2610/20250831/003 | Perlis | Perlis | 11kV | Underground | 31-08-2025 04:09 | PMU KANGAR CB10 | PDB FLAT POLIS KANGAR KAN00517 | PDB FLAT POLIS KANGAR KAN00517 - PDB HOSPITAL BARU KANGAR KAN00499 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 31-08-2025 07:20 | 31-08-2025 07:52 | 32 | 31-08-2025 21:14 | 04-09-2025 22:14 | 97 | 04-09-2025 22:42 | 114.55
Northern | K1 | TRIPPING-KED-25-00609 | 0245/20250831/021 | Kedah | Kuala Nerang | 11kV | Underground | 31-08-2025 07:01 | PPU NAKA 6K5 | PPU NAKA 6K5 | PBT KG. CHANDING KKN00419 - PLT SK LAMDIN KKN00421 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 31-08-2025 07:10 | 31-08-2025 07:45 | 35 | 31-08-2025 17:44 | 02-09-2025 20:11 | 50 | 02-09-2025 21:00 | 61.98
Northern | K1 | TRIPPING-KED-25-00614 | 0242/20250901/036 | Kedah | Jitra | 11kV | Substation | 01-09-2025 15:03 | PPU KODIANG KD5 | PPU KODIANG KD5 | PBT KG. MELELE KJT01290 - | Mechanical | Bushing Damage | None | SWITCHGEAR, CABLE | 01-09-2025 15:10 | 01-09-2025 15:40 | 30 | 05-09-2025 22:45 | 06-09-2025 20:13 | 21 | 06-09-2025 20:20 | 125.28 | 7.25G | 6.43G | 120.4M | 9.00G | 6.81G | 153.1M | 1.24 | 1.08 | 1.27
Northern | K1 | TRIPPING-PLS-25-00075 | RE/2610/20250902/PLS/00075 | Perlis | Perlis | 11kV | Underground | 02-09-2025 20:55 | PMU KUALA PERLIS CB7 | PDB PANGSAPURI KG.WAI KAN02713 |  |  |  |  | NO FAULT | 02-09-2025 20:57 | 02-09-2025 21:30 | 33 |  |  |  | 04-09-2025 16:55 | 44
Northern | K1 | TRIPPING-PLS-25-00076 | 2610/20250903/047 | Perlis | Perlis | 11kV | Overhead | 03-09-2025 21:07 | PPU PADANG BESAR CB7 | PDB KOMP KASTAM & IMIGRESEN KAN00023 CB1 | TOKONG HOCK TECK SOO KAN03049 - PDB PADANG BESAR KAN00036 | Insulation Breakdown | Tree | ABC Conductor | CABLE | 03-09-2025 21:13 | 03-09-2025 21:45 | 32 | 04-09-2025 23:48 | 08-09-2025 22:58 | 95 | 08-09-2025 23:35 | 122.47
Northern | K1 | TRIPPING-KED-25-00626 | 0242/20250905/009 | Kedah | Jitra | 11kV | Underground | 05-09-2025 01:57 | PMU BUKIT KAYU HITAM BKH3 | PMU BUKIT KAYU HITAM BKH3 | PMU BUKIT KAYU HITAM BKH3 - PDB STONE SEAL KJT01112 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 05-09-2025 02:04 | 05-09-2025 02:10 | 6 | 06-09-2025 21:43 | 08-09-2025 20:58 | 47 | 08-09-2025 21:19 | 91.37 | 456M | 461M | 432M | 645M | 647M | 574M | 1.42 | 1.41 | 1.34
Northern | K1 | TRIPPING-KED-25-00632 | 0245/20250909/012 | Kedah | Kuala Nerang | 11kV | Underground | 09-09-2025 09:37 | PPU NAKA 6K5 | PPU NAKA 6K5 | PDB PERUMAHAN LDG SG TEKAI KKN00642 - PBT KG. PADANG-K.NERANG KKN00435 | Insulation Breakdown | Improper Installation | Cable PILC | CABLE | 09-09-2025 09:40 | 09-09-2025 10:15 | 35 | 09-09-2025 16:27 | 12-09-2025 02:09 | 57 | 12-09-2025 23:15 | 85.63 | 3.89G | 1.22G | 1.97G | 4.04G | 1.21G | 1.97G | 1.04 | 0.98 | 1
Northern | K1 | TRIPPING-PLS-25-00077 | 2610/20250913/051 | Perlis | Perlis | 11kV | Underground | 13-09-2025 17:03 | PPU KHEDN 8K5 | PPU KHEDN 8K5 | PPU KHEDN 8K5 - PATOD UJUNG BATU KAN01068 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 13-09-2025 17:05 | 13-09-2025 18:00 | 55 | 14-09-2025 23:50, 23-09-2025 14:35 | 23-09-2025 12:46, 24-09-2025 12:06 | 204, 21 | 24-09-2025 13:15 | 260.2 | 64.6M | 95.5M | 163.2M | 65.4M | 105.1M | 191.7M | 1.01 | 1.1 | 1.18
Northern | K1 | TRIPPING-PLS-25-00078 | 2610/20250913/052 | Perlis | Perlis | 11kV | Underground | 13-09-2025 17:03 | PPU KHEDN 1K5 | PDB TMN SHAHRIZAD KAN00686 | PATOD KLG PERABUT BIDIN KAN02081 - TMN SRI BAKONG KAN02787 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 13-09-2025 17:05 | 13-09-2025 17:21 | 16 | 13-09-2025 22:56 | 17-09-2025 23:30 | 96 | 17-09-2025 23:40 | 102.62 | 135M | 115.4M | 42.4M | 173.4M | 140.7M | 52.2M | 1.28 | 1.23 | 1.77
Northern | K1 | TRIPPING-PLS-25-00079 | 2610/20250915/015 | Perlis | Perlis | 11kV | Underground | 15-09-2025 10:10 | PMU KUALA PERLIS CB11 | PDB KUALA PERLIS KAN01164 CB1 | PVCB BERNAS PADANG JAMIL KAN01214 - PAT KURONG TENGAH KAN02582 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 15-09-2025 10:14 | 15-09-2025 10:46 | 32 | 18-09-2025 11:32 | 21-09-2025 22:23 | 82 | 21-09-2025 22:36 | 156.43 | 84.4G | 83.2G | 94.2G | 102.1G | 105.5G | 123.5G | 1.24 | 1.27 | 1.25
Northern | K1 | TRIPPING-KED-25-00651 | 0242/20250917/081 | Kedah | Jitra | 11kV | Underground | 17-09-2025 20:11 | PPU JERLUN SJ1 | PPU JERLUN SJ1 | PPU JERLUN SJ1 - PLB PEKAN AIR HITAM KJT01419 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 17-09-2025 20:33 | 17-09-2025 21:07 | 34 | 18-09-2025 22:23 | 20-09-2025 23:12 | 48 | 21-09-2025 22:40 | 98.48 | 515M | 418M | 447M | 550M | 499M | 468M | 1.07 | 1.05 | 1.05
Northern | K1 | TRIPPING-PLS-25-00080 | RE/2610/20250921/PLS/00080 | Perlis | Perlis | 11kV | Underground | 21-09-2025 20:48 | PPU UNIMAP GIS 1K5 | SSD UNIMAP ULU PAUH KAN02786 | SSD UNIMAP ULU PAUH KAN02786 - |  |  |  | NO FAULT | 21-09-2025 20:50 | 21-09-2025 21:25 | 35 |  |  |  | 21-09-2025 23:33 | 2.75
Northern | K1 | TRIPPING-KED-25-00658 | 0242/20250922/101 | Kedah | Jitra | 11kV | Underground | 22-09-2025 20:36 | PPU UUM SINTOK ST3 | PPU UUM SINTOK ST3 | PBT KG. BARU SINTOK 1 KJT01002 - STN SUIS KG. PANTONG KJT01622 | Insulation Breakdown | Soil Movement | Cable PILC | CABLE | 22-09-2025 20:38 | 22-09-2025 21:19 | 41 | 23-09-2025 22:20 | 25-09-2025 21:33 | 47 | 25-09-2025 21:53 | 73.28
Northern | K1 | TRIPPING-PLS-25-00081 | 2610/20250923/078 | Perlis | Perlis | 11kV | Overhead | 23-09-2025 03:21 | PMU KUALA PERLIS CB2 | PMU KUALA PERLIS CB2 |  | Insulation Breakdown | Insulation Deterioration | ABC Conductor | NO FAULT | 23-09-2025 03:26 | 23-09-2025 03:40 | 14 |  |  |  | 23-09-2025 03:55 | 0.57
Northern | K1 | TRIPPING-KED-25-00669 | 0242/20250926/044 | Kedah | Jitra | 11kV | Underground | 26-09-2025 12:22 | PPU PELUBANG PL1 | PPU PELUBANG PL1 | PPU PELUBANG PL1 - LOJI AIR PELUBANG KJT00680 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable PILC | CABLE | 26-09-2025 12:23 | 26-09-2025 13:12 | 49 |  |  |  | 27-09-2025 04:25 | 16.05
Northern | K1 | TRIPPING-PLS-25-00082 | 2610/20250928/088 | Perlis | Perlis | 11kV | Overhead | 28-09-2025 02:45 | PMU KUALA PERLIS CB2 | PMU KUALA PERLIS CB2 | PMU KUALA PERLIS CB2 - TMN BUNGA PADI KAN01854 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | OVERHEAD LINES | 28-09-2025 02:50 | 28-09-2025 03:24 | 34 | 28-09-2025 12:03, 09-10-2025 09:06 | 09-10-2025 08:54, 13-10-2025 11:44 | 260, 98 | 14-10-2025 12:27 | 393.7
Northern | K1 | TRIPPING-KED-25-00685 | 0242/20251002/001 | Kedah | Jitra | 11kV | Underground | 02-10-2025 01:59 | PPU CHANGLOON CL3 | PPU CHANGLOON CL3 | PAT RUMAH PAM JALAN KODIANG KJT01608 - PATOD KG. TOK BARUH KJT00988 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 02-10-2025 02:03 | 02-10-2025 02:15 | 12 | 02-10-2025 21:59 | 04-10-2025 21:02 | 47 | 04-10-2025 21:30 | 67.52
Northern | K1 | TRIPPING-PLS-25-00084 | 2610/20251008/028 | Perlis | Perlis | 11kV | Underground | 08-10-2025 05:13 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 | PDB JPJ JEJAWI KAN00748 - PDB SEDC TMN JEJAWI-VVIP KAN00749 | Open Circuit | Soil Movement | Cable PILC | CABLE | 08-10-2025 05:48 | 08-10-2025 05:57 | 9 | 08-10-2025 21:48, 06-11-2025 11:01 | 13-10-2025 12:12, 06-11-2025 21:19 | 110, 10 | 06-11-2025 21:48 | 712.58
Northern | K1 | TRIPPING-PLS-25-00085 | 2610/20251011/019 | Perlis | Perlis | 11kV | Underground | 11-10-2025 11:21 | PMU KANGAR CB16 | PMU KANGAR CB16 | TMN GUAR SYED ALWI KAN02531 - PDB TMN SERI PULAI 4 KAN01802 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 11-10-2025 11:27 | 11-10-2025 11:42 | 15 | 14-10-2025 10:36 | 14-10-2025 22:47 | 12 | 14-10-2025 23:00 | 83.65
Northern | K1 | TRIPPING-KED-25-00704 | 0242/20251012/018 | Kedah | Jitra | 11kV | Overhead | 12-10-2025 14:23 | PPU LOJI AIR ARAU GIS 11K5 | PDB KLG BERAS PERING KJT01776 CB1 | PLB BATAS BENGKOK KJT01414 - R/P MADA MTG KERENG KJT19385 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 12-10-2025 14:30 | 12-10-2025 15:00 | 30 | 12-10-2025 21:46 | 13-10-2025 22:11 | 24 | 13-10-2025 22:21 | 31.97
Northern | K1 | TRIPPING-KED-25-00708 | 0242/20251012/049 | Kedah | Jitra | 11kV | Underground | 12-10-2025 16:47 | PPU CHANGLOON CL6 | PPU CHANGLOON CL6 | STN SUIS R/AWAM CHANGLUN KJT00793 - TMN CASUARINA KJT01810 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 12-10-2025 16:50 | 12-10-2025 17:08 | 18 | 12-10-2025 21:49 | 15-10-2025 22:24 | 72 | 15-10-2025 22:42 | 77.92
Northern | K1 | TRIPPING-PLS-25-00086 | 2610/20251019/077 | Perlis | Perlis | 11kV | Underground | 19-10-2025 23:29 | PPU KHEDN 3K5 | PPU KHEDN 3K5 | PAT TELAGA IDI KAN00604 - QTRS POLIS-KAN KAN00602 | Insulation Breakdown | Soil Movement | Cable PILC | CABLE | 19-10-2025 23:44 | 19-10-2025 23:53 | 9 | 20-10-2025 09:47 | 08-11-2025 06:16 | 452 | 08-11-2025 07:27 | 463.97
Northern | K1 | TRIPPING-KED-25-00734 | 0242/20251022/007 | Kedah | Jitra | 11kV | Overhead | 22-10-2025 07:47 | PMU TANJUNG PAUH TP20 | TMN PELANGI JITRA KJT01863 CB1 | PDB SM P/NYIOR KJT00031 - PDB TMN SRI NYIOR KJT00032 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 22-10-2025 08:20 | 22-10-2025 09:17 | 57 | 22-10-2025 22:00 | 24-10-2025 20:01 | 46 | 24-10-2025 20:10 | 60.38
Northern | K1 | TRIPPING-KED-25-00736 | 0242/20251023/004 | Kedah | Jitra | 11kV | Underground | 23-10-2025 07:04 | PPU LOJI AIR ARAU GIS 11K5 | PDB KLG BERAS PERING KJT01775 CB1 | PDB KLG BERAS PERING KJT01775 - PAT PIDA 12B KJT01341, - PAT PIDA 12B KJT01339 - PBT PIDA 12A KJT01338 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE, CABLE | 23-10-2025 07:07 | 23-10-2025 08:23 | 76 | 23-10-2025 23:15, 24-10-2025 02:15, 25-10-2025 13:15 | 25-10-2025 23:43, 25-10-2025 12:18, 26-10-2025 10:18 | 48, 34, 21 | 26-10-2025 11:06 | 76.03
Northern | K1 | TRIPPING-KED-25-00754 | 0245/20251027/004 | Kedah | Kuala Nerang | 11kV | Underground | 27-10-2025 09:34 | PPU NAKA 4K5 | PDB BDR BARU NAKA KKN00375 CB1 | PDB BDR BARU NAKA KKN00375 - PBT KG. MASJID BARU KKN00377 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 27-10-2025 09:35 | 27-10-2025 10:12 | 37 | 27-10-2025 15:26, 04-11-2025 17:19 | 04-11-2025 17:09, 05-11-2025 05:32 | 193, 12 | 05-11-2025 06:10 | 212.6
Northern | K1 | TRIPPING-PLS-25-00088 | 2610/20251030/024 | Perlis | Perlis | 11kV | Substation | 30-10-2025 14:11 | PPU SHORUBBER CB6 | PDB POLIKLINIK ARAU KAN00902 CB1 |  | Insulation Breakdown | Contamination | None | NO FAULT | 30-10-2025 14:19 | 30-10-2025 14:53 | 34 |  |  |  | 30-10-2025 18:25 | 4.23
Northern | K1 | TRIPPING-KED-25-00768 | 0242/20251101/032 | Kedah | Jitra | 11kV | Underground | 01-11-2025 19:48 | PMU BUKIT KAYU HITAM BKH3 | PMU BUKIT KAYU HITAM BKH3 | PMU BUKIT KAYU HITAM BKH3 - PDB STONE SEAL KJT01112 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 01-11-2025 19:50 | 01-11-2025 20:16 | 26 | 01-11-2025 23:12 | 03-11-2025 23:26 | 48 | 03-11-2025 23:49 | 52.02
Northern | K1 | TRIPPING-KED-25-00770 | 0242/20251103/023 | Kedah | Jitra | 11kV | Substation | 03-11-2025 19:44 | PMU TANJUNG PAUH TP9 | KOMERSIAL SQUARE KOLEJ HEIGHT | KOMERSIAL SQUARE KOLEJ HEIGHT KJT19376 - PDB SM JENAN KJT00554 | Dielectric | Interuption Mechanism Failure | None | CABLE | 03-11-2025 19:50 | 03-11-2025 20:28 | 38 | 04-11-2025 22:29, 07-11-2025 12:02, 11-11-2025 13:09, 13-11-2025 20:03 | 05-11-2025 00:26, 09-11-2025 21:56, 13-11-2025 19:57, 14-11-2025 14:39 | 1, 57, 54, 18 | 14-11-2025 15:16 | 259.53
Northern | K1 | TRIPPING-PLS-25-00089 | 2610/20251106/014 | Perlis | Perlis | 11kV | Overhead | 06-11-2025 04:38 | PPU LOJI AIR ARAU GIS 8K5 | PVCB RUMAH PAM GUAR SANJI KAN00958 | BELAT BATU - PBT HUTAN HANGUS 1 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 06-11-2025 04:42 | 06-11-2025 05:00 | 18 | 11-11-2025 11:10 | 11-11-2025 22:15 | 11 | 11-11-2025 22:55 | 138.28
Northern | K1 | TRIPPING-KED-25-00780 | 0240/20251108/034 | Kedah | Jitra | 11kV | Underground | 08-11-2025 14:09 | PPU DARULAMAN 12K5 | PPU DARULAMAN 12K5 | PDB KLG CHEEST FREEZER KJT00530 - PDB ONKYO KJT00531 | Dielectric | Interuption Mechanism Failure | Cable PILC | CABLE | 08-11-2025 14:12 | 08-11-2025 15:30 | 78 | 08-11-2025 22:24 | 12-11-2025 21:47 | 95 | 12-11-2025 22:09 | 104
Northern | K1 | TRIPPING-KED-25-00781 | 0242/20251108/090 | Kedah | Jitra | 11kV | Underground | 08-11-2025 14:09 | PPU DARULAMAN 9K5 | PPU DARULAMAN 9K5 | PDB I.L.P KJT00158 - PLB PUSAT PEMBIAK IKAN KJT00159 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 08-11-2025 14:12 | 08-11-2025 14:50 | 38 | 10-11-2025 11:53 | 11-11-2025 20:50 | 32 | 11-11-2025 21:04 | 78.92
Northern | K1 | TRIPPING-KED-25-00782 | 0242/20251108/118 | Kedah | Jitra | 11kV | Underground | 08-11-2025 14:09 | PPU DARULAMAN 4K5 | RUMAH KEDAI 50 UNIT KJT19301 | PDB KG. KETUL-KETUL (NOP) KJT00102 - PAT KG. PDG LIMAU KJT00103 | Insulation Breakdown | Mechanical damage due to old external wound | Cable PILC | CABLE | 08-11-2025 14:12 | 08-11-2025 15:51 | 99 | 08-11-2025 22:30 | 13-11-2025 21:00 | 118 | 13-11-2025 21:30 | 127.35
Northern | K1 | TRIPPING-KED-25-00791 | 0245/20251110/003 | Kedah | Kuala Nerang | 11kV | Underground | 10-11-2025 12:08 | PPU KUALA NERANG 10K5 | PBT KG. PADANG NYIOR KKN00302 | PDB SM PADANG SANAI KKN00304 - PBT KG. PADANG NYIOR KKN00302 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 10-11-2025 13:45 | 10-11-2025 14:20 | 35 |  |  |  | 16-11-2025 03:55 | 135.78
Northern | K1 | TRIPPING-PLS-25-00090 | 2610/20251113/008 | Perlis | Perlis | 11kV | Underground | 13-11-2025 10:43 | PPU NEW INDOOR MINI PPU ABI 5K5 | PPU NEW INDOOR MINI PPU ABI 5K5 | PADAT MASJID AL-RAUDAH KAN02908 - PLB KUARI BATU TAN KIM KAN00347 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 13-11-2025 10:50 | 13-11-2025 11:16 | 26 | 16-11-2025 09:46 | 16-11-2025 22:41 | 12 | 16-11-2025 23:17 | 84.57
Northern | K1 | TRIPPING-KED-25-00796 | 0242/20251113/026 | Kedah | Jitra | 11kV | Overhead | 13-11-2025 15:16 | PPU DARULAMAN 1K5 | STN SUIS 11KV IKBN JITRA KJT18896 | PDB KLG NINA MAJU KJT18898 - STN SUIS 11KV IKBN JITRA KJT18896 | Insulation Breakdown | Old External Damage | ABC Conductor | CABLE | 13-11-2025 15:43 | 13-11-2025 16:22 | 39 | 14-11-2025 00:15 | 16-11-2025 22:28 | 70 | 16-11-2025 23:00 | 79.73
Northern | K1 | TRIPPING-PLS-25-00091 | 2610/20251114/017 | Perlis | Perlis | 11kV | Underground | 14-11-2025 03:55 | PMU KUALA PERLIS CB10 | PMU KUALA PERLIS CB10 | PMU KUALA PERLIS CB10 - PDB TMN SEMARAK-KAN KAN00659 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 14-11-2025 04:09 | 14-11-2025 04:37 | 28 | 14-11-2025 23:20, 17-11-2025 08:26 | 17-11-2025 08:24, 17-11-2025 23:16 | 57, 14 | 17-11-2025 23:40 | 91.75
Northern | K1 | TRIPPING-PLS-25-00092 | 2610/20251114/039 | Perlis | Perlis | 11kV | Overhead | 14-11-2025 08:54 | PPU PADANG BESAR CB5 | SSU MRCB CVIA KAN03298 | TPK PELUPUSAN SAMPAH RIMBA MAS KAN02824 - PBT CHECK POINT KAN00094 | Insulation Breakdown | Tree | ABC Conductor | CABLE | 14-11-2025 08:56 | 14-11-2025 09:40 | 44 | 02-12-2025 11:09 | 02-12-2025 23:18 | 12 | 02-12-2025 23:36 | 446.7
Northern | K1 | TRIPPING-KED-25-00809 | 0242/20251116/057 | Kedah | Jitra | 11kV | Overhead | 16-11-2025 22:41 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00742 | PBT KBG BETONG KJT00736 - PDB LOJI PENAPIS AIR KJT19342 | Insulation Breakdown | Old External Damage | ABC Conductor | CABLE | 16-11-2025 22:58 | 16-11-2025 23:06 | 8 | 18-11-2025 09:18 | 20-11-2025 14:49 | 53 | 20-11-2025 14:50 | 88.15
Northern | K1 | TRIPPING-PLS-25-00096 | 2610/20251119/003 | Perlis | Perlis | 11kV | Underground | 19-11-2025 08:30 | PMU KUALA PERLIS CB8 | PDB TMN BUMITA KAN00597 CB1 | PDB TMN BUMITA KAN00597 - PAT TELAGA NYIOR MANIS KAN00677 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 19-11-2025 08:35 | 19-11-2025 08:43 | 8 | 19-11-2025 23:07 | 24-11-2025 01:21 | 98 | 24-11-2025 01:37 | 113.12
Northern | K1 | TRIPPING-KED-25-00815 | 0242/20251119/021 | Kedah | Jitra | 11kV | Underground | 19-11-2025 09:31 | PPU JERLUN SJ1 | PPU JERLUN SJ1 | TMN AROWANA KJT19209 - PP TALIKOM AIR HITAM KJT01441 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 19-11-2025 09:35 | 19-11-2025 09:56 | 21 | 20-11-2025 04:16 | 22-11-2025 20:23 | 64 | 22-11-2025 21:20 | 83.82
Northern | K1 | TRIPPING-KED-25-00816 | 0242/20251119/023 | Kedah | Jitra | 11kV | Underground | 19-11-2025 09:31 | PPU JERLUN SJ6 | PPU JERLUN SJ6 | PPU JERLUN SJ6 - PATOD AIR HITAM KJT01483 | Insulation Breakdown | Soil Movement | Cable PILC | CABLE | 19-11-2025 09:35 | 19-11-2025 09:56 | 21 | 19-11-2025 22:08 | 21-11-2025 05:28 | 31 | 21-11-2025 07:43 | 46.2
Northern | K1 | TRIPPING-KED-25-00819 | 0242/20251119/104 | Kedah | Jitra | 11kV | Underground | 19-11-2025 19:43 | PPU LOJI AIR ARAU GIS 12K5 | PDB KG. KETUL-KETUL KJT00105 CB1 | PAT KG. KETUL KJT00083 - PDB KG. KETUL-KETUL (NOP) KJT00082 | Insulation Breakdown | Mechanical damage due to old external wound | Cable PILC | CABLE | 19-11-2025 19:46 | 19-11-2025 20:28 | 42 | 20-11-2025 02:30, 20-11-2025 18:23 | 20-11-2025 18:21, 20-11-2025 19:31 | 15, 1 | 21-11-2025 06:20 | 34.62
Northern | K1 | TRIPPING-PLS-25-00097 | 2610/20251120/018 | Perlis | Perlis | 11kV | Underground | 20-11-2025 14:16 | PPU SHORUBBER CB7 | PDB TMN HARMONI KANGAR KAN01924 | PDB SRI PERLIS INN KAN00506 - PDB PUTRA PALACE B KAN00507 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 20-11-2025 14:20 | 20-11-2025 14:51 | 31 | 30-11-2025 11:17 | 30-11-2025 22:41 | 11 | 30-11-2025 22:56 | 248.67
Northern | K1 | TRIPPING-KED-25-00824 | 0242/20251121/039 | Kedah | Jitra | 11kV | Underground | 21-11-2025 04:52 | PPU CHANGLOON CL2 | PDB TMN MERBAU KJT01859 CB1 | PATOD KG. BARU KJT00853 - STN SUIS KG. LANGSAT KJT00854 | Insulation Breakdown | Soil Movement | Cable XLPE | CABLE | 21-11-2025 04:55 | 21-11-2025 05:38 | 43 | 21-11-2025 22:00 | 23-11-2025 20:29 | 46 | 23-11-2025 21:21 | 64.48
Northern | K1 | TRIPPING-PLS-25-00098 | 2610/20251121/010 | Perlis | Perlis | 11kV | Underground | 21-11-2025 09:36 | PPU PADANG BESAR CB11 | PPU PADANG BESAR CB11 | PDB HALAL HUB KAN02416 - SK FELDA RIMBA MAS KAN02414 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 21-11-2025 09:40 | 21-11-2025 10:30 | 50 | 21-11-2025 22:18 | 26-11-2025 23:33 | 121 | 26-11-2025 23:45 | 134.15
Northern | K1 | TRIPPING-PLS-25-00099 | RE/2610/20251121/PLS/00099 | Perlis | Perlis | 11kV | Underground | 21-11-2025 11:21 | PPU BUKIT KETERI 1K5 | PDB TMN SRI PUTERI KAN02605 | PDB TMN SRI PUTERI KAN02605 - |  |  |  | NO FAULT | 21-11-2025 11:21 | 21-11-2025 12:01 | 40 |  |  |  | 21-11-2025 22:00 | 10.65
Northern | K1 | TRIPPING-KED-25-00829 | 0242/20251124/014 | Kedah | Jitra | 11kV | Underground | 24-11-2025 08:34 | PPU PELUBANG 3K5 | PPU PELUBANG 3K5 | PBT KOTA MENGKUANG KJT00688 - PDB SK PENGHULU HJ DARUS KJT00692 | Open Circuit | Soil Movement | Cable PILC | CABLE | 24-11-2025 08:37 | 24-11-2025 09:05 | 28 | 24-11-2025 22:10 | 27-11-2025 21:41 | 71 | 27-11-2025 21:55 | 85.35
Northern | K1 | TRIPPING-KED-25-00830 | 0242/20251124/081 | Kedah | Jitra | 11kV | Underground | 24-11-2025 21:25 | PMU BUKIT KAYU HITAM BKH5 | BAYAN MAS NO.2 KJT01825 CB1 | PDB KOMP LAKA TEMIN KJT01100 - PDB BALAI POLIS LAKA TEMIN-NOP KJT01101 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 24-11-2025 21:35 | 24-11-2025 22:35 | 60 | 25-11-2025 22:34 | 26-11-2025 21:43 | 23 | 26-11-2025 22:14 | 48.82
Northern | K1 | TRIPPING-PLS-25-00100 | 2610/20251125/010 | Perlis | Perlis | 11kV | Underground | 25-11-2025 01:44 | PPU KHEDN 6K5 | PPU KHEDN 6K5 | PDB R/KDAI PENGKALAN ASAM KAN00427 - PDB BILIK SEJUK FAMA KAN00428 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 25-11-2025 01:57 | 25-11-2025 02:08 | 11 | 25-11-2025 18:24, 08-01-2026 10:21 | 08-01-2026 09:57, 13-01-2026 00:35 | 1047, 110 | 13-01-2026 01:05 | 1175.35
Northern | K1 | TRIPPING-PLS-25-00101 | 2610/20251125/012 | Perlis | Perlis | 11kV | Overhead | 25-11-2025 02:09 | PPU PADANG BESAR CB2 | PEKAN KAKI BUKIT KAN00139 CB1 | PDB BDR BARU WANG KELIAN KAN00158 - CSU VIEW POINT KAN03349 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 25-11-2025 02:10 |  | 0 | 30-11-2025 15:19 | 02-12-2025 11:13 | 43 | 03-12-2025 09:40 | 199.52
Northern | K1 | TRIPPING-KED-25-00832 | 0242/20251125/011 | Kedah | Jitra | 11kV | Underground | 25-11-2025 07:18 | PPU JERLUN SJ2 | PPU JERLUN SJ2 | PPU JERLUN SJ2 - PDB KLG PROSES UDANG KERPAN KJT01686 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 25-11-2025 07:21 | 25-11-2025 08:13 | 52 | 25-11-2025 23:07 | 06-12-2025 10:05 | 250 | 06-12-2025 10:15 | 266.95
Northern | K1 | TRIPPING-KED-25-00842 | 0245/20251126/006 | Kedah | Kuala Nerang | 11kV | Underground | 26-11-2025 15:46 | PPU KUALA NERANG 7K5 | A/R GENTING PALAS | SSL GENTING PALAS KKN00078 - PBT BUKIT NAMBUA KKN00082 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 26-11-2025 16:20 | 26-11-2025 16:28 | 8 | 27-11-2025 17:11 | 28-11-2025 12:19 | 19 | 28-11-2025 12:55 | 45.15
Northern | K1 | TRIPPING-PLS-25-00102 | 2610/20251129/158 | Perlis | Perlis | 11kV | Substation | 29-11-2025 13:32 | PMU CHUPING TXF31 | PMU CHUPING TXF31 | TAE HWA KAN00225 - PLB FERMPRO KAN00226, CPNG CB30, FLASHOVER - | Dielectric | Dielectric Deterioration | None | BUSBAR, CABLE, CABLE | 29-11-2025 13:40 | 29-11-2025 14:22 | 42 | 30-11-2025 16:38 | 01-12-2025 09:40 | 17 | 01-12-2025 10:12 | 44.67
Northern | K1 | TRIPPING-PLS-25-00103 | 2610/20251130/003 | Perlis | Perlis | 11kV | Underground | 30-11-2025 08:36 | PPU LOJI AIR ARAU GIS 5K5 | PPU LOJI AIR ARAU GIS 5K5 | PDB BERNAS ARAU KAN00905 - PDB ISTANA ARAU-VVIP KAN00904 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 30-11-2025 08:39 | 30-11-2025 09:17 | 38 | 30-11-2025 14:13 | 27-12-2025 00:19 | 634 | 27-12-2025 00:30 | 639.9
Northern | K1 | TRIPPING-KED-25-00853 | 0242/20251201/040 | Kedah | Jitra | 11kV | Underground | 01-12-2025 22:15 | PPU MINI PPU KERPAN KRPN 5K5 | PPU MINI PPU KERPAN KRPN 5K5 | PBT KUALA SANGLANG 1 KJT01581 - PBT KUALA SANGLANG 2 KJT01582 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 01-12-2025 22:18 | 01-12-2025 22:50 | 32 | 02-12-2025 21:12 | 04-12-2025 21:59 | 48 | 04-12-2025 22:10 | 71.92
Northern | K1 | TRIPPING-PLS-25-00104 | 2610/20251202/007 | Perlis | Perlis | 11kV | Substation | 02-12-2025 08:21 | PPU PADANG BESAR CB12 | RPA PADANG BESAR KAN02911 CB1 |  | Dielectric breakdown | Shorted By Animal | None | NO FAULT | 02-12-2025 08:23 | 02-12-2025 08:40 | 17 |  |  |  | 02-12-2025 08:41 | 0.33
Northern | K1 | TRIPPING-PLS-25-00105 | 2610/20251204/022 | Perlis | Perlis | 11kV | Underground | 04-12-2025 13:35 | PMU KANGAR CB12 | PVCB TMN MERPATI KAN00716 CB1 | PDB TMN FIRDAUS KANGAR KAN00540 - PDB PANGSAPURI SERI SENA KAN00541 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 04-12-2025 13:39 | 04-12-2025 13:59 | 20 | 12-12-2025 20:47 | 13-12-2025 14:45 | 17 | 13-12-2025 14:55 | 217.33
Northern | K1 | TRIPPING-KED-25-00861 | 0242/20251206/012 | Kedah | Jitra | 11kV | Underground | 06-12-2025 06:38 | PMU BUKIT KAYU HITAM BKH4 | PMU BUKIT KAYU HITAM BKH4 | SSD NO.1 KJT00824 - PAT BATU 26 KJT19463 | Insulation Breakdown | Soil Movement | Cable PILC | CABLE | 06-12-2025 06:42 | 06-12-2025 07:11 | 29 | 06-12-2025 22:30 | 09-12-2025 22:00 | 71 | 11-12-2025 15:21 | 128.72
Northern | K1 | TRIPPING-PLS-25-00106 | 2610/20251206/052 | Perlis | Perlis | 11kV | Underground | 06-12-2025 19:27 | PPU SHORUBBER CB4 | PVCB TMN JALI KAN02329 CB1 | PDB TMN KEMAJUAN 1 KAN00582 - PDB TMN KEMAJUAN 2 KAN00581 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 06-12-2025 19:28 | 06-12-2025 19:55 | 27 | 11-12-2025 11:08 | 11-12-2025 23:06 | 11 | 11-12-2025 23:20 | 123.88
Northern | K1 | TRIPPING-PLS-25-00107 | 2610/20251208/002 | Perlis | Perlis | 11kV | Underground | 08-12-2025 00:22 | PPU PADANG BESAR CB5 | SSU MRCB CVIA KAN03298 CB1 | PBT CHECK POINT KAN00095 - PDB BATU BERTANGKUP KAN00096 | Insulation Breakdown | Soil Movement | Cable PILC | CABLE | 08-12-2025 00:33 | 08-12-2025 00:56 | 23 | 10-12-2025 10:10 | 10-12-2025 22:46 | 12 | 10-12-2025 23:00 | 70.63
Northern | K1 | TRIPPING-PLS-25-00108 | 2610/20251210/013 | Perlis | Perlis | 11kV | Underground | 10-12-2025 10:23 | PPU UNIMAP GIS 2K5 | FELDA CHUPING NO.2 KAN02701 CB1 | FELDA CHUPING NO.2 KAN02701 - PDB FELDA CHUPING 3 KAN00249 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 10-12-2025 10:24 | 10-12-2025 11:09 | 45 | 10-12-2025 23:27 | 16-12-2025 00:27 | 121 | 16-12-2025 00:43 | 134.33
Northern | K1 | TRIPPING-KED-25-00870 | 0242/20251210/021 | Kedah | Jitra | 11kV | Substation | 10-12-2025 16:29 | PMU TANJUNG PAUH TP19 | PMU TANJUNG PAUH TP19 | PLB PUSAT KESIHATAN JITRA KJT00174 - | Mechanical | - | None | SWITCHGEAR | 10-12-2025 16:33 | 10-12-2025 16:44 | 11 | 10-12-2025 22:55 | 11-12-2025 02:07 | 3 | 11-12-2025 02:43 | 10.23
Northern | K1 | TRIPPING-PLS-25-00109 | 2610/20251215/031 | Perlis | Perlis | 11kV | Underground | 15-12-2025 17:20 | PMU KANGAR CB2 | PDB TELEKOM LAMA KANGAR KAN00548 CB1 | PDB TELEKOM LAMA KANGAR KAN00548 - HOSPITAL TUANKU FAUZIAH KAN02622 | Open Circuit | Soil Movement | Cable PILC | CABLE |  |  | 0 | 17-12-2025 00:23, 24-12-2025 11:16 | 22-12-2025 20:53, 25-12-2025 09:04 | 140, 21 | 25-12-2025 09:08 | 231.8
Northern | K1 | TRIPPING-KED-25-00880 | 0242/20251215/043 | Kedah | Jitra | 11kV | Underground | 15-12-2025 18:40 | PPU DARULAMAN 6K5 | PPU DARULAMAN 6K5 | PDB HOSPITAL JITRA KJT00458 - PDB TNB JITRA KJT00457 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 15-12-2025 18:42 | 15-12-2025 18:54 | 12 | 15-12-2025 23:26 | 15-01-2026 21:09 | 741 | 15-01-2026 21:58 | 747.3
Northern | K1 | TRIPPING-KED-25-00884 | 0245/20251217/010 | Kedah | Kuala Nerang | 11kV | Underground | 17-12-2025 12:05 | PPU KUALA NERANG 10K5 | PPU KUALA NERANG 10K5 | KRC 2 KKN00856 - KRC KKN00846 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 17-12-2025 12:13 | 17-12-2025 12:43 | 30 | 17-12-2025 20:08 | 24-12-2025 21:21 | 169 | 24-12-2025 21:29 | 177.4
Northern | K1 | TRIPPING-KED-25-00885 | 0245/20251217/011 | Kedah | Kuala Nerang | 11kV | Overhead | 17-12-2025 12:23 | PPU KUALA NERANG 6K5 | PPU KUALA NERANG 6K5 | PATOD KG. SENA BAKONG KKN00072 - KG RAMBUTAN KKN00838 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 17-12-2025 12:59 | 17-12-2025 13:20 | 21 | 18-12-2025 21:13 | 19-12-2025 02:07 | 4 | 19-12-2025 02:30 | 38.12
Northern | K1 | TRIPPING-PLS-25-00110 | 2610/20251217/032 | Perlis | Perlis | 11kV | Underground | 17-12-2025 12:32 | PPU SHORUBBER CB6 | PDB POLIKLINIK ARAU KAN00902 CB1 | TMN ARAU UTAMA KAN01992 - PDB RANI ESTATE KAN00853 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE, CABLE | 17-12-2025 12:47 | 17-12-2025 13:00 | 13 | 22-12-2025 12:29 | 22-12-2025 22:41 | 10 | 22-12-2025 00:00 | 107.47
Northern | K1 | TRIPPING-PLS-25-00112 | 2610/20251217/162 | Perlis | Perlis | 11kV | Underground | 17-12-2025 22:24 | PPU UNIMAP GIS 2K5 | PPU UNIMAP GIS 2K5 | PDB KOK KELANG 2 KAN00250 - FELDA CHUPING NO.2 KAN02698 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 17-12-2025 22:37 | 17-12-2025 22:43 | 6 | 18-12-2025 20:53, 23-12-2025 10:07 | 22-12-2025 20:50, 23-12-2025 23:57 | 95, 13 | 24-12-2025 04:00 | 149.6
Northern | K1 | TRIPPING-PLS-25-00113 | 2610/20251220/017 | Perlis | Perlis | 11kV | Underground | 20-12-2025 15:05 | PPU KHEDN 5K5 | PPU KHEDN 5K5 | PDB BUKIT LAGI NO.2 KAN01897 - PDB BANDARAN(NOP) KAN00438 | Insulation Breakdown | Mechanical damage due to old external wound | Cable PILC | CABLE | 20-12-2025 15:12 | 20-12-2025 15:28 | 16 | 24-12-2025 22:17 | 27-12-2025 11:02 | 60 | 27-12-2025 11:04 | 163.98
Northern | K1 | TRIPPING-PLS-25-00114 | 2610/20251222/022 | Perlis | Perlis | 11kV | Underground | 22-12-2025 09:56 | PPU PADANG BESAR CB2 | FISHING NET KAN00068 CB1 | BT 20 RUMAH PAM KAN00078 - PDB TMN PADANG BESAR INDAH KAN03088 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 22-12-2025 10:20 | 22-12-2025 10:55 | 35 | 23-12-2025 18:12, 27-01-2026 12:32 | 04-01-2026 11:42, 28-01-2026 02:24 | 281, 13 | 28-01-2026 02:35 | 880.65
Northern | K1 | TRIPPING-KED-25-00899 | 0242/20251222/015 | Kedah | Jitra | 11kV | Underground | 22-12-2025 11:36 | PPU CHANGLOON CL3 | PPU CHANGLOON CL3 | PDB R/AWAM CHANGLUN KJT00970 - PLB PEKAN CHANGLUN 1 KJT00971 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 22-12-2025 11:43 | 22-12-2025 12:00 | 17 | 22-12-2025 22:20 | 29-12-2025 22:16 | 167 | 29-12-2025 22:25 | 178.82
Northern | K1 | TRIPPING-KED-25-00903 | 0245/20251222/008 | Kedah | Kuala Nerang | 11kV | Overhead | 22-12-2025 15:52 | PPU NAKA 3K5 | PPU NAKA 3K5 | PLB TANDOP BESAR KKN00166 - PAT PONG MANIS UTARA KKN00168 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE, CABLE | 22-12-2025 15:55 | 22-12-2025 16:10 | 15 | 23-12-2025 17:10 | 24-12-2025 12:14 | 19 | 24-12-2025 13:10 | 45.3
Northern | K1 | TRIPPING-KED-25-00912 | 0245/20251224/006 | Kedah | Kuala Nerang | 11kV | Substation | 24-12-2025 08:22 | PPU NAKA 4K5 | PPU NAKA 4K5 |  | Dielectric breakdown | Shorted By Animal | None | TRANSIENT | 24-12-2025 08:24 | 24-12-2025 09:08 | 44 |  |  |  | 24-12-2025 10:22 | 2
Northern | K1 | TRIPPING-KED-25-00914 | 0245/20251224/026 | Kedah | Kuala Nerang | 11kV | Overhead | 24-12-2025 16:33 | PPU NAKA 3K5 | PPU NAKA 3K5 | PADAT LADANG AYAM KG BAROKHAS KKN00781 - PDB LOJI AIR KUALA NERANG KKN00109 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 24-12-2025 16:36 | 24-12-2025 16:58 | 22 | 24-12-2025 17:55 | 26-12-2025 11:23 | 41 | 26-12-2025 11:43 | 43.17
Northern | K1 | TRIPPING-PLS-25-00115 | 2610/20251225/066 | Perlis | Perlis | 11kV | Underground | 25-12-2025 20:39 | PPU SHORUBBER CB4 | PVCB TMN JALI KAN02329 CB1 | PDB LPN KANGAR KAN00566 - PDB JALAN RAJA SYED ALWI KAN00569 | Insulation Breakdown | Soil Movement | Cable PILC | CABLE | 25-12-2025 20:41 | 25-12-2025 20:50 | 9 | 26-12-2025 22:18, 29-12-2025 10:11 | 28-12-2025 14:10, 29-12-2025 23:11 | 39, 13 | 29-12-2025 23:24 | 98.75
Northern | K1 | TRIPPING-KED-25-00919 | 0245/20251230/008 | Kedah | Jitra | 11kV | Underground | 30-12-2025 09:23 | PPU KUALA NERANG 7K5 | PPU KUALA NERANG 7K5 | TMN SRI TAMPOI KKN00669 - LADANG BATU HITAM KKN00738 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 30-12-2025 09:26 | 30-12-2025 10:00 | 34 | 03-01-2026 13:31 | 03-01-2026 21:12 | 7 | 03-01-2026 21:32 | 108.15
Northern | K1 | TRIPPING-KED-25-00921 | 0242/20251230/010 | Kedah | Jitra | 11kV | Underground | 30-12-2025 13:41 | PMU BUKIT KAYU HITAM BKH10 | PLB SMPG BKT.TANGGA KJT00879 CB1 | QTRS UPP(KBG PASU) KJT01709 - PDT KOTA DELAPAN 2 KJT19545 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable PILC | CABLE | 30-12-2025 14:30 | 30-12-2025 15:00 | 30 | 30-12-2025 23:15 | 31-12-2025 21:06 | 21 | 31-12-2025 21:17 | 31.6
Northern | K1 | TRIPPING-PLS-25-00116 | 2610/20251231/018 | Perlis | Perlis | 11kV | Underground | 31-12-2025 11:57 | PPU SHORUBBER CB2 | PDB ALOR LANCANG KAN00833 CB1 | PDT KUKUM KUBANG GAJAH KAN00831 - PDB SK KUBANG GAJAH KAN00830 | Insulation Breakdown | Mechanical damage due to old external wound | Cable PILC | CABLE | 31-12-2025 12:00 | 31-12-2025 12:18 | 18 | 01-01-2026 00:20, 06-01-2026 08:21 | 01-01-2026 10:57, 06-01-2026 23:30 | 10, 15 | 06-01-2026 23:53 | 155.93
Northern | K1 | TRIPPING-PLS-25-00117 | 2610/20251231/048 | Perlis | Perlis | 11kV | Underground | 31-12-2025 21:43 | PPU POLITEKNIK PAUH PERLIS 2 | PPU POLITEKNIK PAUH PERLIS CB2 | MRSM ULU PAUH KAN02114 - TMN KURUNG ANAI KAN02837 | Open Circuit | Improper Installation | Cable XLPE | CABLE | 31-12-2025 21:50 | 31-12-2025 22:10 | 20 | 01-01-2026 23:16, 04-01-2026 11:50 | 04-01-2026 11:47, 05-01-2026 09:34 | 60, 21 | 05-01-2026 09:56 | 108.22 | 894m | 841m | 767m | 1.296G | 1.135G | 1.059G | 1.46 | 1.41 | 1.38
Northern | K1 | TRIPPING-PLS-26-00001 | 2610/20260102/012 | Perlis | Perlis | 11kV | Substation | 02-01-2026 03:56 | PPU SIMPANG EMPAT CB9 | PPU SIMPANG EMPAT CB9 | PAT PADANG BENTA-VVIP - | Dielectric breakdown | Shorted By Animal | None | TRANSIENT | 02-01-2026 03:59 | 02-01-2026 04:30 | 31 |  |  |  | 02-01-2026 04:31 | 0.58
Northern | K1 | TRIPPING-KED-26-00004 | 0242/20260102/043 | Kedah | Jitra | 11kV | Underground | 02-01-2026 11:23 | PMU BUKIT KAYU HITAM BKH4 | PDB PROTAB AGROBASE KJT01138 CB1 | SSD NO.1 KJT00824 - PAT BATU 26 KJT19463 | Insulation Breakdown | Soil Movement | Cable PILC | CABLE | 02-01-2026 11:32 | 02-01-2026 11:55 | 23 | 02-01-2026 16:20 | 04-01-2026 00:27 | 32 | 04-01-2026 00:32 | 37.15 | 126.0M | 111.9M | 97.2M | 155.2M | 132.6M | 100.3M | 1.24 | 1.2 | 1.03
Northern | K1 | TRIPPING-KED-26-00007 | 0242/20260102/069 | Kedah | Jitra | 11kV | Substation | 02-01-2026 19:22 | PPU JERLUN SJ1 | PPU JERLUN SJ1 | PLB KLG CHUAN HIN KJT01472 - SM SANGLANG (SANG) KJT01473 | Dielectric | Vermin Encroachment | None | CABLE | 02-01-2026 19:27 | 02-01-2026 20:00 | 33 | 02-01-2026 20:58 | 03-01-2026 21:44 | 24 | 03-01-2026 22:05 | 26.72 | 170.3M | 158.0M | 177.2M | 220M | 198.9M | 229M | 1.3 | 1.26 | 1.29
Northern | K1 | TRIPPING-PLS-26-00002 | 2610/20260103/047 | Perlis | Perlis | 11kV | Underground | 03-01-2026 20:09 | PMU CHUPING CB7 | PDB KUBANG PERUN KAN00255 | SK PANGGAS KAN02286 - PVCB PANGGAS KAN00282 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 03-01-2026 20:27 | 03-01-2026 20:30 | 3 | 03-01-2026 21:20, 07-01-2026 09:29 | 07-01-2026 08:42, 08-01-2026 23:44 | 83, 38 | 08-01-2026 23:53 | 123.73 | 261M | 265M | 244M | 287.1M | 291.5M | 263.52M | 1.1 | 1.1 | 1.08
Northern | K1 | TRIPPING-KED-26-00015 | 0242/20260108/009 | Kedah | Jitra | 11kV | Underground | 08-01-2026 15:21 | PMU BUKIT KAYU HITAM BKH11 | PMU BUKIT KAYU HITAM BKH11 | PMU BUKIT KAYU HITAM BKH11 - SS KLG ACM NO.2 KJT18969 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 08-01-2026 15:25 | 08-01-2026 15:56 | 31 | 08-01-2026 22:27 | 10-01-2026 20:26 | 45 | 10-01-2026 20:41 | 53.33 | 18.39G | 25.0G | 32.1G | 18.23G | 27.7G | 39.4G | 0.98 | 1.1 | 1.04
Northern | K1 | TRIPPING-PLS-26-00003 | 2610/20260109/037 | Perlis | Perlis | 11kV | Underground | 09-01-2026 17:57 | PPU NEW INDOOR MINI PPU ABI 3K5 | PPU NEW INDOOR MINI PPU ABI 3K5 | PLB KUARI BATU SYED OMAR 1 KAN00337 - PLB SMPG SYED OMAR KAN00338 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | NO FAULT | 09-01-2026 18:00 | 09-01-2026 18:23 | 23 | 09-01-2026 21:54 | 10-01-2026 23:24 | 25 | 11-01-2026 00:27 | 30.5 | 308M | 321M | 284M | 354.2M | 375.6M | 326.6M | 1.15 | 1.17 | 1.15
Northern | K1 | TRIPPING-KED-26-00028 | 0242/20260111/006 | Kedah | Jitra | 11kV | Underground | 11-01-2026 14:45 | PPU DARULAMAN 10K5 | PPU DARULAMAN 10K5 | PPU DARULAMAN 10K5 - PDB TMN GEMILANG (JIT) KJT01696 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 11-01-2026 14:49 | 11-01-2026 14:49 | 0 | 11-01-2026 21:08 | 12-01-2026 21:36 | 24 | 12-01-2026 22:17 | 31.53 | 740M | 676M | 640M | 751M | 690M | 641M | 1.01 | 1.05 | 1.01
Northern | K1 | TRIPPING-PLS-26-00004 | 2610/20260113/056 | Perlis | Perlis | 11kV | Underground | 13-01-2026 21:59 | PMU CHUPING CB1 | PMU CHUPING CB1 | PLB 132KV PMU CHUPING (LUAR) KAN00262 - PDT KG.BALIK BUKIT KAN00264 | Insulation Breakdown | Improper Installation | Cable XLPE | CABLE | 13-01-2026 22:08 | 13-01-2026 22:36 | 28 | 15-01-2026 08:39 | 15-01-2026 16:55 | 8 | 15-01-2026 17:19 | 43.33 | 12.26G | 17.17G | 14.40G | 12.75G | 18.2G | 16.1G | 1.04 | 1.06 | 1.12
Northern | K1 | TRIPPING-KED-26-00041 | 0242/20260116/008 | Kedah | Jitra | 11kV | Underground | 16-01-2026 02:28 | PPU CHANGLOON CL2 | PDB TMN MERBAU KJT01859 CB1 | PBT SHELL CHANGLUN KJT00827 - PDB TMN SRI CHANGLUN 1 KJT00828 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 16-01-2026 02:32 | 16-01-2026 03:01 | 29 | 16-01-2026 11:11 | 21-01-2026 21:39 | 130 | 21-01-2026 21:44 | 139.27 | 512M | 554M | 579M | 745M | 842M | 898M | 1.46 | 1.52 | 1.56
Northern | K1 | TRIPPING-PLS-26-00005 | 2610/20260120/043 | Perlis | Perlis | 11kV | Underground | 20-01-2026 14:42 | PPU LOJI AIR ARAU GIS 5K5 | PPU LOJI AIR ARAU GIS 5K5 | PBT MADA GUAR SANJI KAN00948 - PAT MADA KURUNG ANAI KAN00949 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 20-01-2026 14:54 | 20-01-2026 15:10 | 16 | 20-01-2026 21:38 | 23-01-2026 22:43 | 73 | 23-01-2026 23:06 | 80.4 | 3.33G | 3.28G | 3.54G | 3.36G | 4.89G | 3.58G | 1.01 | 1.49 | 1.01
Northern | K1 | TRIPPING-PLS-26-00006 | 2610/20260120/060 | Perlis | Perlis | 11kV | Substation | 20-01-2026 16:37 | PPU PADANG BESAR CB12 | RPA PADANG BESAR KAN02911 CB1 | SEK KEB PADANG BESAR (U) KAN03290 - PAT KG. MELAYU KAN00040 | Others | Others | None | CABLE | 20-01-2026 16:40 | 20-01-2026 17:24 | 44 | 01-02-2026 11:51 | 01-02-2026 21:43 | 9 | 01-02-2026 22:31 | 293.9 | 186M | 204M | 190M |  |  |  | 1.02 | 1.03 | 1.02
Northern | K1 | TRIPPING-KED-26-00053 | 0242/20260121/054 | Kedah | Jitra | 11kV | Underground | 21-01-2026 20:02 | PMU TANJUNG PAUH TP9 | PMU TANJUNG PAUH TP9 | PDB MACRO DIMENSION KJT00572 - PDB TMN KELISA-JITRA KJT00573 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 21-01-2026 20:05 | 21-01-2026 20:44 | 39 | 21-01-2026 22:32 | 22-01-2026 21:44 | 23 | 22-01-2026 21:50 | 25.8 | 914M | 1.179G | 926M | 930M | 1.190G | 936M | 1.02 | 1.01 | 1.01
Northern | K1 | TRIPPING-KED-26-00057 | 0242/20260122/052 | Kedah | Jitra | 11kV | Underground | 22-01-2026 17:36 | PMU TANJUNG PAUH TP20 | KLG DOUBLE SITE KJT01578 CB1 | PDB TMN CAHAYA-JITRA KJT00010 - PDT TMN SERI PADANG KJT18939 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 22-01-2026 17:51 | 22-01-2026 18:00 | 9 | 22-01-2026 21:55 | 24-01-2026 21:40 | 47 | 24-01-2026 22:15 | 52.65 | 1.921G | 1.552G | 2.05G | 2.03G | 1.630G | 2.15G | 1.07 | 1.05 | 1.05
Northern | K1 | TRIPPING-PLS-26-00007 | 2610/20260123/010 | Perlis | Perlis | 11kV | Underground | 23-01-2026 12:31 | PPU SHORUBBER CB10 | PPU SHORUBBER CB10 |  | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 23-01-2026 12:40 | 23-01-2026 13:10 | 30 | 24-01-2026 00:19 | 24-01-2026 23:42 | 23 | 25-01-2026 01:10 | 36.65 | 187M | 208M | 161M |  |  |  | 1.1 | 1.07 | 1.09
Northern | K1 | TRIPPING-PLS-26-00008 | 2610/20260126/050 | Perlis | Perlis | 11kV | Underground | 26-01-2026 10:50 | PPU SHORUBBER CB8 | PDB SMPG ABI KAN00315 CB1 | PAT ABI TOK HASHIM KAN00363 - PDB SK BEHOR EMPIANG KAN00364 | Insulation Breakdown | Soil Movement | Cable PILC | CABLE | 26-01-2026 10:51 |  | 0 | 26-01-2026 21:28 | 28-01-2026 22:27 | 48 | 28-01-2026 22:44 | 59.9 | 157M | 152M | 168M |  |  |  | 1.01 | 1.01 | 1.01
Northern | K1 | TRIPPING-PLS-26-00010 | 2610/20260126/099 | Perlis | Perlis | 11kV | Underground | 26-01-2026 15:09 | PMU KANGAR CB1 | PDB SEKOLAH VOKASIONAL KANGAR KAN00472 CB1 | PDB SK SRI INDRA KAN00470 - PDB PERPUSTAKAAN NEGERI-PPNPS KAN00469 | Insulation Breakdown | Soil Movement | Cable PILC | CABLE | 26-01-2026 15:11 | 26-01-2026 15:50 | 39 | 28-01-2026 16:47 | 28-01-2026 23:47 | 6 | 29-01-2026 00:05 | 56.93 | 169M | 152M | 188M |  |  |  | 1.05 | 1.03 | 1.02
Northern | K1 | TRIPPING-PLS-26-00011 | 2610/20260126/153 | Perlis | Perlis | 11kV | Underground | 26-01-2026 22:07 | PMU CHUPING CB4 | PDB TMN DESA PAUH KAN00925 | TAPAK PELUPUSAN SPH PDG SIDING KAN02807 - PBT PADANG SIDING-VVIP KAN00873 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 26-01-2026 22:35 | 26-01-2026 22:55 | 20 | 28-01-2026 00:40 | 29-01-2026 21:50 | 45 | 29-01-2026 22:15 | 72.13 | 533M | 508M | 631M |  |  |  | 1.29 | 1.29 | 1.32
Northern | K1 | TRIPPING-PLS-26-00012 | 2610/20260128/016 | Perlis | Perlis | 11kV | Underground | 28-01-2026 15:00 | PMU CHUPING CB7 | PDB KUBANG PERUN KAN00255 | KG. CHELONG KAN03376 - PAT KG. PADANG JELUTONG KAN00796 | Open Circuit | Soil Movement | Cable PILC | CABLE | 28-01-2026 15:02 | 28-01-2026 15:30 | 28 | 29-01-2026 01:37 | 31-01-2026 21:59 | 68 | 31-01-2026 22:13 | 79.22 | 141M | 169M | 154M |  |  |  | 1.11 | 1.1 | 1.11
Northern | K1 | TRIPPING-KED-26-00076 | 0242/20260129/005 | Kedah | Jitra | 11kV | Underground | 29-01-2026 10:28 | PPU UUM SINTOK ST5 | S/S KLJ PERTANIAN BKT TANGGA KJT01848 CB1 | PATOD KG. BARU PADONG - PDB BALAI POLIS LAKA TEMIN-NOP KJT01071 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable PILC | CABLE | 29-01-2026 10:30 | 29-01-2026 11:00 | 30 | 31-01-2026 22:46 | 01-02-2026 23:09 | 24 | 01-02-2026 23:27 | 84.98 | 133.4M | 166.9M | 133.0M | 177.2M | 215M | 168.6M | 1.26 | 1.33 | 1.25
Northern | K1 | TRIPPING-PLS-26-00013 | 2610/20260201/034 | Perlis | Perlis | 11kV | Underground | 01-02-2026 22:18 | PMU KUALA PERLIS CB10 | PMU KUALA PERLIS CB10 | PMU KUALA PERLIS CB10 - PDB TMN SEMARAK-KAN KAN00659 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 01-02-2026 22:22 |  | 0 | 02-02-2026 21:33 | 08-02-2026 22:15 | 144 | 08-02-2026 22:41 | 168.38 | 115M | 130M | 138M |  |  |  | 1.09 | 1.1 | 1.1
Northern | K1 | TRIPPING-PLS-26-00014 | 2610/20260203/027 | Perlis | Perlis | 11kV | Overhead | 03-02-2026 17:07 | PPU SHORUBBER CB7 | PPU SHORUBBER CB7 | PPU SHORUBBER CB7 - MEDAN TANJUNG GORA-VVIP KAN03007 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | OVERHEAD LINES | 03-02-2026 17:24 | 03-02-2026 17:49 | 25 | 03-02-2026 22:21 | 04-02-2026 22:57 | 24 | 04-02-2026 23:14 | 30.12 | 41.3G | 39.9G | 22.5G |  |  |  | 1.22 | 1.16 | 1.09
Northern | K1 | TRIPPING-KED-26-00088 | 0242/20260204/022 | Kedah | Jitra | 11kV | Underground | 04-02-2026 16:10 | PPU DARULAMAN 7K5 | SSD KLG ISO TECH KJT00519 | SSD INFRA STRUKTUR TG PAUH KJT00503 - S/S NICHIAS KJT00507 |  |  |  | CABLE | 04-02-2026 16:52 | 04-02-2026 17:12 | 20 | 04-02-2026 21:57 | 05-02-2026 21:04 | 23 | 05-02-2026 21:11 | 29.02 | 1.109G | 997M | 1.003G | 1.267G | 1.067G | 1.031G | 1.14 | 1.4 | 1.07
Northern | K1 | TRIPPING-PLS-26-00015 | 2610/20260207/014 | Perlis | Perlis | 11kV | Underground | 07-02-2026 10:02 | PMU CHUPING CB3 | PMU CHUPING CB3 | KG. GIAL KAN02364 - PDB UITM ARAU KAN00867 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable XLPE | CABLE | 07-02-2026 10:06 | 07-02-2026 10:35 | 29 | 07-02-2026 22:38 | 11-02-2026 20:43 | 94 | 11-02-2026 20:50 | 106.8 | 310M | 380M | 523M |  |  |  | 1.08 | 1.09 | 1.09
Northern | K1 | TRIPPING-PLS-26-00016 | 2610/20260208/003 | Perlis | Perlis | 11kV | Underground | 08-02-2026 00:54 | PMU KUALA PERLIS CB8 | PMU KUALA PERLIS CB8 | PDB BALAI BOMBA KUALA PERLIS KAN01904 - PDB KRAF TANGAN KAN00669 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 08-02-2026 01:04 |  | 0 | 09-02-2026 17:07 | 15-02-2026 10:10 | 137 | 15-02-2026 10:31 | 177.62 | 155M | 171M | 141M |  |  |  | 1.01 | 1.01 | 1.02
Northern | K1 | TRIPPING-PLS-26-00017 | 2610/20260209/026 | Perlis | Perlis | 11kV | Underground | 09-02-2026 11:26 | PMU KUALA PERLIS CB12 | PDB KUALA PERLIS KAN01162 | PDB UPP KUALA PERLIS KAN00665 - PDB TMN BERLIAN-KAN KAN00664 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 09-02-2026 12:03 | 09-02-2026 12:39 | 36 | 10-02-2026 00:35, 10-02-2026 01:00 | 10-02-2026 00:43, 13-02-2026 15:42 | 0, 86 | 13-02-2026 15:45 | 100.32 | 55.9M | 55.2M | 49.2M |  |  |  | 1 | 1 | 1
Northern | K1 | TRIPPING-PLS-26-00018 | 2610/20260210/001 | Perlis | Perlis | 11kV | Underground | 10-02-2026 06:40 | PPU SIMPANG EMPAT CB1 | PDB KLG PADI MAJU KAN01041 CB1 | PAT PADANG PETANI KAN01050 - PDB KLG BERAS KUDUNG KAN01051 | Insulation Breakdown | Soil Movement | Cable PILC | CABLE | 10-02-2026 06:52 | 10-02-2026 07:20 | 28 | 11-02-2026 22:39 | 14-02-2026 09:15 | 58 | 14-02-2026 09:46 | 99.1 | 137.2M | 175.2M | 127.3M |  |  |  | 1.05 | 1.05 | 1.05
Northern | K1 | TRIPPING-KED-26-00107 | 0242/20260212/072 | Kedah | Jitra | 11kV | Underground | 12-02-2026 20:46 | PMU TANJUNG PAUH TP15 | PDB TMN PASU KJT00468 CB1 | PDB MADA JITRA KJT00480 - PDB TMN SETIA JAYA-JITRA KJT00484 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 12-02-2026 20:49 | 12-02-2026 20:55 | 6 | 13-02-2026 21:38 | 16-02-2026 22:06 | 72 | 16-02-2026 22:12 | 97.43 | 61.3M | 56.2M | 50.1M | 61.8M | 56.4M | 53.2M | 1.38 | 1 | 1
Northern | K1 | TRIPPING-KED-26-00110 | 0242/20260213/019 | Kedah | Jitra | 11kV | Underground | 13-02-2026 10:20 | PPU CHANGLOON CL1 | SEK MEN CHANGLUN KJT00895 CB1 | PBT PADANG ASUN KJT18958 - PBT PAYA KEMUNTING ESTATE KJT00947 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable PILC | CABLE | 13-02-2026 10:28 | 13-02-2026 10:45 | 17 | 13-02-2026 22:59 | 14-02-2026 21:34 | 22 | 14-02-2026 21:38 | 35.3 | 730M | 701M | 705M | 1.080G | 1.084G | 1.096G | 1.5 | 1.55 | 1.55
Northern | K1 | TRIPPING-PLS-26-00019 | 2610/20260217/036 | Perlis | Perlis | 11kV | Substation | 17-02-2026 16:51 | PPU SHORUBBER CB5 | BEHOR MENTALOON KAN00974 CB1 | PAT SEMUT GATAL-VVIP - | Dielectric breakdown | Shorted By Animal | None | SWITCHGEAR | 17-02-2026 16:54 | 17-02-2026 17:20 | 26 |  |  |  | 17-02-2026 18:44 | 1.88
Northern | K1 | TRIPPING-PLS-26-00021 | 2610/20260223/008 | Perlis | Perlis | 11kV | Overhead | 23-02-2026 11:01 | PPU UNIMAP GIS 2K5 | FELDA CHUPING NO.2 KAN02702 CB1 | FELDA CHUPING NO.2 KAN02702 - PDB FELDA CHUPING 1 KAN00245 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | OVERHEAD LINES | 23-02-2026 11:04 | 23-02-2026 11:45 | 41 | 23-02-2026 22:12 | 25-02-2026 01:28 | 27 | 25-02-2026 01:45 | 38.73 | 29.6G | 31.3G | 30.6G |  |  |  | 1.22 | 1.05 | 1.12
Northern | K1 | TRIPPING-PLS-26-00022 | 2610/20260224/008 | Perlis | Perlis | 11kV | Underground | 24-02-2026 11:03 | PPU BUKIT KETERI 6K5 | PDB TMN BESERI JAYA KAN00176 CB1 | P/E ALUR LIMPAH BARAT KAN02724 - PDB VCB TIMAH TASOH KAN00171 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 24-02-2026 11:09 | 24-02-2026 11:35 | 26 | 25-02-2026 16:38 | 26-02-2026 01:37 | 8 | 26-02-2026 01:45 | 38.7 | 1.023G | 1.448G | 1.211G |  |  |  | 1.12 | 1.19 | 1.39
Northern | K1 | TRIPPING-PLS-26-00023 | 2610/20260225/004 | Perlis | Perlis | 11kV | Overhead | 25-02-2026 04:47 | PPU PADANG BESAR CB2 | PEKAN KAKI BUKIT KAN00139 CB1 | CSU VIEW POINT KAN03349 - PDB BDR BARU WANG KELIAN KAN00158 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | OVERHEAD LINES | 25-02-2026 05:05 | 25-02-2026 06:05 | 60 | 01-03-2026 12:36 | 01-03-2026 23:23 | 10 | 02-03-2026 22:14 | 137.45 | 368M | 470M | 327M |  |  |  | 1.08 | 1.01 | 1.01
Northern | K1 | TRIPPING-PLS-26-00024 | 2610/20260226/006 | Perlis | Perlis | 11kV | Underground | 26-02-2026 04:39 | PMU KUALA PERLIS CB12 | PDB DIBUK SYNERGY KAN01260 CB1 | PDT KUKUM AUTO MART KAN01270 - PDT KLG TEPONG KAN01271 | Insulation Breakdown | Old External Damage | Cable PILC | CABLE | 26-02-2026 04:41 | 26-02-2026 05:15 | 34 | 28-02-2026 17:03 | 01-03-2026 09:58 | 16 | 01-03-2026 12:05 | 79.43 | 505M | 638M | 486M |  |  |  | 1.23 | 1.27 | 1.21
Northern | K1 | TRIPPING-KED-26-00146 | 0242/20260228/061 | Kedah | Jitra | 11kV | Overhead | 28-02-2026 20:48 | PPU JERLUN SJ7 | PPU JERLUN SJ7 | TMN BAWAL KJT19099 - SS 11KV SAMAK KJT18976 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | OVERHEAD LINES | 28-02-2026 20:51 | 28-02-2026 21:42 | 51 | 01-03-2026 00:18 | 02-03-2026 14:15 | 37 | 03-03-2026 21:03 | 72.25 | 211M | 101.5M | 103.4M | 237M | 102.5M | 104.9M | 1.09 | 1.01 | 1.01
Northern | K1 | TRIPPING-KED-26-00151 | 0245/20260302/010 | Kedah | Kuala Nerang | 11kV | Underground | 02-03-2026 17:05 | PPU NAKA 4K5 | PPU NAKA 4K5 | PDB QTRS GURU NAKA KKN00362 - PADAT KLINIK KESIHATAN NAKA KKN00732 | Insulation Breakdown | Old External Damage | Cable XLPE | CABLE | 02-03-2026 17:06 | 02-03-2026 17:40 | 34 | 03-03-2026 01:29 | 04-03-2026 21:21 | 43 | 04-03-2026 21:39 | 52.57 | 3.16G | 2.39G | 2.27G | 5.19G | 3.22G | 2.96G | 1.67 | 1.35 | 1.32
Northern | K1 | TRIPPING-KED-26-00153 | 0242/20260304/026 | Kedah | Jitra | 11kV | Overhead | 04-03-2026 13:32 | PMU TANJUNG PAUH TP6 | BELLEZA GARDEN HOMES KJT18927 CB1 | PDT TMN BKT TINGGI KJT19249 - PDB SK BKT TINGGI KJT00408 | Insulation Breakdown | Mechanical damage due to old external wound | ABC Conductor | CABLE | 04-03-2026 13:34 | 04-03-2026 14:01 | 27 | 04-03-2026 16:34 | 07-03-2026 20:54 | 76 | 07-03-2026 21:00 | 79.47 | 60.1G | 62.6G | 74.2G | 72.9G | 66.7G | 74.3G | 1.07 | 1.12 | 1
Northern | K1 | TRIPPING-PLS-26-00025 | 2610/20260305/082 | Perlis | Perlis | 11kV | Underground | 05-03-2026 23:49 | PMU KANGAR CB11 | PMU KANGAR CB11 | PAT ABI TOK HASHIM KAN00363 - PDB SK BEHOR EMPIANG KAN00364 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 05-03-2026 23:50 | 06-03-2026 00:13 | 23 | 08-03-2026 21:30 | 12-03-2026 18:30 | 92 | 12-03-2026 18:45 | 162.93 | 144.4M | 220M | 167.8M |  |  |  | 1.06 | 1.09 | 1.05
Northern | K1 | TRIPPING-PLS-26-00026 | 2610/20260310/020 | Perlis | Perlis | 11kV | Underground | 10-03-2026 13:27 | PMU CHUPING CB6 | PMU CHUPING CB6 | PDB KOK KELANG 2 KAN00250 - FELDA CHUPING NO.2 KAN02698 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 10-03-2026 13:34 | 10-03-2026 14:00 | 26 | 12-03-2026 22:02 | 16-03-2026 14:19 | 88 | 17-03-2026 10:07 | 164.67 | 110.4M | 118.3M | 137.6M |  |  |  | 1.18 | 1.2 | 1.22
Northern | K1 | TRIPPING-PLS-26-00027 | 2610/20260312/078 | Perlis | Perlis | 11kV | Underground | 12-03-2026 17:23 | PPU BUKIT KETERI 1K5 | PPU BUKIT KETERI 1K5B | PAT TASIK MELATI KAN00774 - KG BONGKOK SANTAN KAN02814 | Open Circuit | Soil Movement | Cable PILC | CABLE | 12-03-2026 17:31 | 12-03-2026 17:52 | 21 | 13-03-2026 22:02 | 14-03-2026 14:44 | 16 | 14-03-2026 14:57 | 45.57 | 511M | 328M | 448M |  |  |  | 1.14 | 1.02 | 1.08
Northern | K1 | TRIPPING-PLS-26-00028 | 2610/20260314/029 | Perlis | Perlis | 11kV | Underground | 14-03-2026 21:46 | PPU PADANG BESAR CB5 | UKK PADANG BESAR KAN00047 CB1 | TPK PELUPUSAN SAMPAH RIMBA MAS KAN02824 - PBT CHECK POINT KAN00094 | Insulation Breakdown | Improper Installation | Cable PILC | CABLE | 14-03-2026 21:55 | 14-03-2026 22:50 | 55 | 15-03-2026 17:11, 16-03-2026 22:38 | 15-03-2026 22:46, 17-03-2026 09:57 | 5, 11 | 18-03-2026 10:26 | 84.67 | 118.9M | 208M | 288M |  |  |  | 1.25 | 1.33 | 1.18
Northern | K1 | TRIPPING-KED-26-00199 | 0242/20260318/143 | Kedah | Jitra | 11kV | Underground | 18-03-2026 21:51 | PPU JERLUN SJ6 | PPU JERLUN SJ6 | PPU JERLUN SJ6 - PATOD AIR HITAM KJT01483 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 18-03-2026 21:56 | 18-03-2026 22:38 | 42 | 19-03-2026 00:44 | 21-03-2026 05:53 | 53 | 21-03-2026 06:04 | 56.22 | 43.7M | 44.1M | 48.2M | 48.0M | 46.7M | 56.3M | 1.09 | 1.17 | 1.14
Northern | K1 | TRIPPING-KED-26-00200 | 0242/20260319/172 | Kedah | Jitra | 11kV | Substation | 19-03-2026 23:10 | PPU KODIANG KD5 | PPU KODIANG KD5 | PBT KG. MELELE KJT01285 - | Insulation Breakdown | Insulation Deterioration | None | SWITCHGEAR | 19-03-2026 23:14 | 20-03-2026 00:01 | 47 | 20-03-2026 12:28 | 20-03-2026 21:04 | 8 | 20-03-2026 21:16 | 22.1
Northern | K1 | TRIPPING-KED-26-00202 | 0242/20260320/599 | Kedah | Jitra | 11kV | Underground | 20-03-2026 20:52 | PPU LOJI AIR ARAU GIS 12K5 | PPU LOJI AIR ARAU GIS 12K5 | PLB LPN LANA BULU KJT01312 - PATOD R/PAM MADA MEGAT DEWA KJT18985 | Mechanical | Damage Enclosure | Cable PILC | CABLE | 20-03-2026 21:07 | 20-03-2026 21:25 | 18 | 21-03-2026 03:17 | 22-03-2026 03:05 | 23 | 22-03-2026 03:17 | 30.42 | 1.723G | 1.634G | 2.31G | 1.920G | 1.91G | 2.64G | 1.15 | 1.17 | 1.22
Northern | K1 | TRIPPING-PLS-26-00030 | 2610/20260330/007 | Perlis | Perlis | 11kV | Underground | 30-03-2026 00:30 | PMU KUALA PERLIS CB10 | PDB TMN SEMARAK KAN00657 CB1 | PDB TMN SEMARAK-KAN KAN00657 - PDB IKBN KUALA PERLIS KAN00656, - CSU KUARTERS IKBN KAN03251 - PDB PELADANG JAYA KAN00652 | Open Circuit | Improper Installation | Cable PILC | CABLE, CABLE, CABLE | 30-03-2026 00:32 | 30-03-2026 01:07 | 35 | 30-03-2026 21:48 | 31-03-2026 18:22 | 20 | 31-03-2026 18:38 | 42.13
Northern | K1 | TRIPPING-KED-26-00248 | 0242/20260403/016 | Kedah | Jitra | 11kV | Underground | 03-04-2026 06:16 | PPU CHANGLOON CL4 | PPU CHANGLOON CL4 | C/SUB TAMAN NAPOH KJT19292 - TMN JELUTONG FASA 2 KJT19192 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 03-04-2026 06:21 | 03-04-2026 06:37 | 16 | 03-04-2026 22:55 | 04-04-2026 21:11 | 22 | 04-04-2026 21:49 | 39.55 | 170.1M | 114.6M | 134.6M | 189.0M | 138.7M | 177.0M | 1.11 | 1.23 | 1.26
Northern | K1 | TRIPPING-PLS-26-00031 | 2610/20260412/006 | Perlis | Perlis | 11kV | Overhead | 12-04-2026 05:02 | PMU CHUPING CB7 | PDB KUBANG PERUN KAN00255 | SMK GUAR NANGKA KAN02148 - KG. CHELONG KAN03375 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 12-04-2026 05:05 | 12-04-2026 05:40 | 35 | 13-04-2026 09:11, 13-04-2026 11:25 | 13-04-2026 11:05, 15-04-2026 00:46 | 1, 37 | 15-04-2026 01:15 | 68.22
Northern | K1 | TRIPPING-PLS-26-00032 | 2610/20260414/014 | Perlis | Perlis | 11kV | Overhead | 14-04-2026 08:15 | PPU SHORUBBER CB5 | PDB BEHOR MENTALOON KAN00974 | BEHOR MENTALOON KAN00974 - PLB BEHOR MENTALOON KAN00986 | Insulation Breakdown | Vandalism / Encroachment | ABC Conductor | CABLE | 14-04-2026 08:29 | 14-04-2026 09:04 | 35 | 17-04-2026 08:31 | 17-04-2026 21:25 | 12 | 17-04-2026 21:58 | 85.72
Northern | K1 | TRIPPING-PLS-26-00033 | 2610/20260414/048 | Perlis | Perlis | 11kV | Underground | 14-04-2026 16:25 | PPU PADANG BESAR CB10 | PBT FRIM KAN00113 | PLB S.SUIS SMPG KAKI BUKIT KAN00165 - PBT WANG MU KAN00167 | Insulation Breakdown | Tree | Cable PILC | CABLE | 14-04-2026 16:50 | 14-04-2026 17:52 | 62 | 14-04-2026 22:02 | 16-04-2026 02:45 | 28 | 16-04-2026 02:56 | 34.52
Northern | K1 | TRIPPING-PLS-26-00034 | 2610/20260416/124 | Perlis | Perlis | 11kV | Underground | 16-04-2026 00:20 | PMU KUALA PERLIS CB2 | PDB TAMAN BUNGA PADI KAN00389 | PBT KG TELOK JAMBU KAN00394 - PDB TMN MAS MUDA KAN02024 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 16-04-2026 00:26 | 16-04-2026 00:50 | 24 | 19-04-2026 18:55 | 20-04-2026 12:31 | 17 | 20-04-2026 12:51 | 108.52
Northern | K1 | TRIPPING-PLS-26-00035 | 2610/20260416/147 | Perlis | Perlis | 11kV | Underground | 16-04-2026 17:21 | PPU PADANG BESAR CB5 | SSU MRCB CVIA KAN03298 | TPK PELUPUSAN SAMPAH RIMBA MAS KAN02824 - PBT CHECK POINT KAN00094 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 16-04-2026 17:24 | 16-04-2026 18:15 | 51 | 16-04-2026 20:59 | 18-04-2026 12:20 | 39 | 18-04-2026 12:43 | 43.37
Northern | K1 | TRIPPING-KED-26-00282 | 0245/20260417/065 | Kedah | Kuala Nerang | 11kV | Overhead | 17-04-2026 23:37 | PPU NAKA 1K5 | PPU NAKA 1K5 | PLB REBAN AYAM PONG KKN03050 - PBT KEDA NAKA KKN00398 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 17-04-2026 23:57 | 18-04-2026 00:10 | 13 | 19-04-2026 15:04 | 22-04-2026 02:03 | 58 | 22-04-2026 02:12 | 98.58 | 6.98G | 8.72G | 3.77G | 9.01G | 9.91G | 4.56G | 1.29 | 1.14 | 1.21
Northern | K1 | TRIPPING-PLS-26-00036 | 2610/20260418/029 | Perlis | Perlis | 11kV | Underground | 18-04-2026 12:56 | PPU SHORUBBER CB4 | TAMAN JALI KAN02329 | PDB TMN KEMAJUAN 1 KAN00582 - PDB TMN KEMAJUAN 2 KAN00581 | Open Circuit | Improper Installation | Cable XLPE | CABLE | 18-04-2026 13:00 | 18-04-2026 13:20 | 20 | 18-04-2026 22:04 | 21-04-2026 11:34 | 61 | 21-04-2026 12:00 | 71.07
Northern | K1 | TRIPPING-KED-26-00291 | 0242/20260420/015 | Kedah | Jitra | 11kV | Underground | 20-04-2026 13:00 | PMU BUKIT KAYU HITAM BKH10 | PDB QRTS UPP BKT KAYU HITAM KJT01709 | QTRS UPP(KBG PASU) KJT01709 - PDT DATARAN BKH KJT19585 |  |  |  | CABLE | 20-04-2026 15:40 | 20-04-2026 15:50 | 10 | 20-04-2026 20:59 | 22-04-2026 23:09 | 50 | 22-04-2026 23:16 | 58.27 | 1.662G | 1.278G | 1.78G | 2.43G | 1.671G | 2.71G | 1.47 | 1.33 | 1.51
Northern | K1 | TRIPPING-KED-26-00298 | 0245/20260422/041 | Kedah | Kuala Nerang | 11kV | Underground | 22-04-2026 23:25 | PPU KUALA NERANG 7K5 | PPU KUALA NERANG 7K5 | PLB BKT TEMBAGA KKN00103 - PBT KUALA PAI KKN00105 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 22-04-2026 23:30 | 22-04-2026 23:50 | 20 | 26-04-2026 11:35 | 26-04-2026 18:49 | 7 | 26-04-2026 21:26 | 94.02 | 151.7M | 163.9M | 157.5M | 190.5M | 208M | 195.4M | 1.27 | 1.28 | 1.24
Northern | K1 | TRIPPING-KED-26-00308 | 0242/20260426/083 | Kedah | Jitra | 11kV | Underground | 26-04-2026 14:06 | PPU DARULAMAN 9K5 | PPU DARULAMAN 9K5 | PPU DARULAMAN 9K5 - PDB I.L.P KJT01718 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 26-04-2026 14:19 | 26-04-2026 14:43 | 24 | 26-04-2026 22:24 | 29-04-2026 22:41 | 72 | 29-04-2026 23:29 | 81.38 | 280M | 242M | 240M | 382M | 274M | 311M | 1.16 | 1.15 | 1.16
Northern | K1 | TRIPPING-KED-26-00310 | 0242/20260427/007 | Kedah | Jitra | 11kV | Substation | 27-04-2026 03:29 | PPU JERLUN SJ4 | PDB KLG BERAS SUPREME KJT01676 | STN OPERASI KTMB SG KOROK KJT18981 - STN KTMB TUNJANG KJT19013 | Mechanical | Bushing Damage | None | CABLE | 27-04-2026 03:36 | 27-04-2026 04:30 | 54 | 27-04-2026 22:39, 05-05-2026 10:05 | 05-05-2026 10:03, 05-05-2026 17:40 | 179, 7 | 05-05-2026 18:20 | 206.85
Northern | K1 | TRIPPING-KED-26-00322 | 0242/20260430/021 | Kedah | Jitra | 11kV | Underground | 30-04-2026 03:39 | PMU TANJUNG PAUH TP6 | PDB TMN BELLEZA GARDEN HOMES KJT18927 | PDT KG. ALOR RAMBAI KJT19509 - PDB TMN TABUNG HJ KJT00405 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 30-04-2026 03:51 | 30-04-2026 04:22 | 31 | 30-04-2026 21:08 | 03-05-2026 21:54 | 72 | 03-05-2026 22:04 | 90.42 | 486M | 510M | 505M | 596M | 631M | 567M | 1.22 | 1.24 | 1.2
Northern | K1 | TRIPPING-PLS-26-00038 | RE/2610/20260503/00038 | Perlis | Perlis | 11kV | Underground | 03-05-2026 18:48 | PPU UNIMAP GIS 1K5 | SSD UNIMAP ULU PAUH KAN02786 |  |  |  |  | NO FAULT | 03-05-2026 18:48 | 03-05-2026 19:20 | 32 |  |  |  | 03-05-2026 23:18 | 4.5
Northern | K1 | TRIPPING-PLS-26-00039 | 2610/20260505/012 | Perlis | Perlis | 11kV | Overhead | 05-05-2026 09:41 | PMU CHUPING CB7 | PDB KUBANG PERUN KAN00255 | KG. CHELONG KAN03375 - SMK GUAR NANGKA KAN02148 | Insulation Breakdown | - | ABC Conductor | CABLE | 05-05-2026 09:55 | 05-05-2026 10:12 | 17 | 06-05-2026 12:52 | 07-05-2026 00:42 | 11 | 07-05-2026 00:57 | 39.27 | 2.07G | 3.25G | 2.65G | 2.30G | 4.12G | 2.72G | 1 | 1.04 | 1.03
Northern | K1 | TRIPPING-KED-26-00344 | 0242/20260506/035 | Kedah | Jitra | 11kV | Underground | 06-05-2026 06:03 | PPU DARULAMAN 3K5 | PPU DARULAMAN 3K5 | PATOD KG. PENIA KJT00234 - PDB SK MALAU KJT00235 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 06-05-2026 06:18 | 06-05-2026 06:45 | 27 | 06-05-2026 12:01 | 09-05-2026 23:07 | 83 | 09-05-2026 23:29 | 89.43
Northern | K1 | TRIPPING-PLS-26-00041 | 2610/20260507/096 | Perlis | Perlis | 11kV | Underground | 07-05-2026 17:33 | PMU CHUPING CB8 | PMU CHUPING CB8 | PMU CHUPING CB8 - TAE HWA KAN00223 | Open Circuit | Soil Movement | Cable PILC | CABLE | 07-05-2026 17:40 |  | 0 | 08-05-2026 16:59 | 11-05-2026 01:18 | 56 | 12-05-2026 01:05 | 103.53 | 1.284G | 1.087G | 985M | 1.324G | 1.111G | 1.0210G | 1.04 | 1.02 | 1.04
Northern | K1 | TRIPPING-KED-26-00352 | 0242/20260510/098 | Kedah | Jitra | 11kV | Underground | 10-05-2026 21:09 | PPU DARULAMAN 8K5 | PDB TMN TG SARINA 6 KJT19072 | PDB LOJI KUMBAHAN KJT00644 - PDB SM DARUL AMAN HEIGHT KJT01856 | Open Circuit | Soil Movement | Cable XLPE | CABLE | 10-05-2026 21:15 | 10-05-2026 21:30 | 15 | 11-05-2026 18:16, 20-05-2026 12:26 | 20-05-2026 11:16, 22-05-2026 00:29 | 209, 36 | 22-05-2026 00:34 | 267.42
Northern | K1 | TRIPPING-PLS-26-00042 | 2610/20260512/016 | Perlis | Perlis | 11kV | Underground | 12-05-2026 08:42 | PMU KANGAR CB13 | PMU KANGAR CB13 | PMU KANGAR CB13 - PVCB SHOERUBBER KAN00738 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 12-05-2026 08:42 | 12-05-2026 09:10 | 28 | 12-05-2026 09:40, 12-05-2026 22:28 | 12-05-2026 09:53 | 0 |  | 0 | 221.5M | 240M | 277M | 312.1M | 300M | 316M | 1.11 | 1.25 | 1.31
Northern | K1 | TRIPPING-KED-26-00371 | 0242/20260516/075 | Kedah | Jitra | 11kV | Underground | 16-05-2026 23:05 | PPU CHANGLOON CL1 | PDB SM CHANGLUN KJT00742 | PATOD CHANGKAT NIBONG KJT00739 - PBT KBG BETONG KJT00738 | Insulation Breakdown | Mechanical damage due to old external wound | Cable PILC | CABLE | 16-05-2026 23:07 | 16-05-2026 23:18 | 11 | 17-05-2026 19:24 | 19-05-2026 22:48 | 51 | 19-05-2026 22:52 | 71.78
Northern | K1 | TRIPPING-PLS-26-00043 | 2610/20260517/042 | Perlis | Perlis | 11kV | Underground | 17-05-2026 05:38 | PPU SHORUBBER CB2 | PPU SHORUBBER CB2 | PPU SHORUBBER CB2 - PDB ALOR LANCANG KAN00835 | Open Circuit | Soil Movement | Cable PILC | CABLE | 17-05-2026 06:08 | 17-05-2026 06:40 | 32 | 18-05-2026 20:34 | 21-05-2026 09:21 | 60 | 21-05-2026 09:52 | 100.23 | 732M | 1.380M | 1.204G | 1.060G | 2.28G | 2.01G | 1.45 | 1.67 | 1.66
Northern | K1 | TRIPPING-KED-26-00385 | 0242/20260521/019 | Kedah | Jitra | 11kV | Underground | 21-05-2026 17:23 | PPU JERLUN SJ6 | JERLUN A/R PIDA 5 | PAT KG. KETUL-VVIP KJT00083 - PDB KG. KETUL-KETUL (NOP) KJT00082 | Insulation Breakdown | Mechanical damage due to old external wound | Cable PILC | CABLE | 21-05-2026 18:10 | 21-05-2026 18:54 | 44 | 22-05-2026 21:44, 23-05-2026 20:26 | 23-05-2026 20:20, 23-05-2026 21:35 | 22, 1 | 23-05-2026 21:50 | 52.45
Northern | K1 | TRIPPING-PLS-26-00045 | 2610/20260528/053 | Perlis | Perlis | 11kV | Substation | 28-05-2026 14:18 | PPU SHORUBBER CB6 | PDB POLIKLINIK ARAU KAN00902 |  | Others | Others | None | NO FAULT | 28-05-2026 14:34 | 28-05-2026 14:50 | 16 |  |  |  | 28-05-2026 15:26 | 1.13
Northern | K1 | TRIPPING-PLS-26-00046 | 2610/20260530/006 | Perlis | Perlis | 11kV | Overhead | 30-05-2026 08:53 | PMU CHUPING CB1 | KAJI CUACA KAN00789 | CSU SOLAR KBJ HECMY KAN03140 - TMN TOK KAYAMAN KAN03142 | Insulation Breakdown | Tree | ABC Conductor |  | 30-05-2026 09:59 | 30-05-2026 10:20 | 21 | 30-05-2026 17:28 |  |  |  | 0 | 111.56M | 119.59M | 133.9M | 112.61M | 122.2M | 137.7M | 1.09 | 1.14 | 1.11
Northern | K1 | TRIPPING-KED-26-00425 | 0245/20260602/003 | Kedah | Kuala Nerang | 11kV | Underground | 02-06-2026 04:45 | PPU KUALA NERANG 1K5 | KUALA NERANG 1K5 | PAT LENGKONG PEDU :KKN00832 - PBT SS BULUH BESAR :KKN00339 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 02-06-2026 04:52 | 02-06-2026 05:16 | 24 | 02-06-2026 06:16 | 03-06-2026 20:25 | 38 | 03-06-2026 21:54 | 41.15
Northern | K1 | TRIPPING-PLS-26-00047 | 2610/20260603/061 | Perlis | Perlis | 11kV | Substation | 03-06-2026 19:58 | PPU SHORUBBER 6 | PDB POLIKLINIK ARAU KAN00902 | PDB RUMAH PAM ARAU :KAN0050 - | Others | Others | None | NO FAULT | 03-06-2026 20:05 | 03-06-2026 20:30 | 25 | 10-06-2026 18:36 | 10-06-2026 18:48 | 0 | 10-06-2026 19:33 | 167.58
Northern | K1 | TRIPPING-KED-26-00440 | 0245/20260605/005 | Kedah | Kuala Nerang | 11kV | Underground | 05-06-2026 15:34 | PPU NAKA 6K5 | NAKA 33 6K5 | PBT KG. WAN LAH :KPG00438 - PAT KG. LINCAN :KPG00439 | Insulation Breakdown | Mechanical damage due to 3rd Party Excavation | Cable PILC | CABLE | 05-06-2026 15:35 | 05-06-2026 16:10 | 35 | 06-06-2026 21:53 | 07-06-2026 04:52 | 6 | 07-06-2026 23:50 | 56.27 | 6.96G | 6.54G | 4.88G | 7.46G | 6.82G | 5.13G | 1.08 | 1.07 | 1.07
Northern | K1 | TRIPPING-KED-26-00450 | 0245/20260607/004 | Kedah | Kuala Nerang | 11kV | Overhead | 07-06-2026 12:27 | PPU PEDU KKN00798 | PEDU KKN00798 | PBT SIMPANG EMPAT PEDU :KKN00646 - PAT KG. TONG PELU :KKN00147 | Insulation Breakdown | Insulation Deterioration | ABC Conductor | CABLE | 07-06-2026 12:36 | 07-06-2026 12:55 | 19 | 07-06-2026 22:06 | 08-06-2026 21:44 | 23 | 08-06-2026 22:15 | 33.8 | 88.0M | 87.3M | 82.8M | 88.7M | 87.9M | 82.6M | 1.01 | 1.01 | 1
Northern | K1 | TRIPPING-KED-26-00457 | 0242/20260609/045 | Kedah | Jitra | 11kV | Underground | 09-06-2026 18:05 | PMU TANJUNG PAUH TP15 | PDB TMN PASU KJT00468 | PDB MADA JITRA :KJT00480 - PDB TMN SETIA JAYA-JITRA :KJT00484, PDB TMN SETIA JAYA-JITRA :KJT00486 - PDB LLM JLN BKT WANG :KJT00487 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 09-06-2026 18:06 | 09-06-2026 18:20 | 14 | 09-06-2026 22:37, 09-06-2026 22:40 | 10-06-2026 22:04, 10-06-2026 09:13 | 23, 10 | 10-06-2026 22:39 | 28.57
Northern | K1 | TRIPPING-PLS-26-00049 | 2610/20260610/023 | Perlis | Perlis | 11kV | Underground | 10-06-2026 07:43 | PPU UNIMAP GIS - UMAP 2K5 | PDB PERLIS PLANTATION KAN00237 | - - | Insulation Breakdown | Insulation Deterioration | Cable PILC | NO FAULT | 10-06-2026 07:47 | 10-06-2026 08:29 | 42 |  |  |  | 10-06-2026 09:18 | 1.58 | 2.09G | 6.24G | 5.02G | 2.16G | 7.06G | 5.31G | 1.05 | 1.14 | 1.06
Northern | K1 | TRIPPING-KED-26-00486 | 0242/20260621/021 | Kedah | Jitra | 11kV | Overhead | 21-06-2026 01:36 | PPU KODIANG KD1 | PBT RUMAH PAM PERING KJT01152 | PAT TOK ARANG 2 :KJT19251 - PBT KG. TOK ARANG 1 :KJT19250 | Insulation Breakdown | Tree | ABC Conductor | CABLE | 21-06-2026 01:37 | 21-06-2026 02:21 | 44 | 21-06-2026 11:37 | 22-06-2026 08:50 | 21 | 22-06-2026 09:14 | 31.63
Northern | K1 | TRIPPING-PLS-26-00051 | 2610/20260625/015 | Perlis | Perlis | 11kV | Substation | 25-06-2026 08:10 | PPU UNIMAP GIS - UMAP 2K5 | PDB PERLIS PLANTATION KAN00237 | PERLIS PLANTATION :KAN00237 - | Dielectric | Vandalism / Encroachment | None | TRANSIENT | 25-06-2026 08:16 | 25-06-2026 08:35 | 19 |  |  |  | 25-06-2026 09:13 | 1.05 | 198.9M | 238.2M | 258M | 206.0M | 256.3M | 266M | 1.04 | 1 | 1.02
Northern | K1 | TRIPPING-KED-26-00501 | 0242/20260627/014 | Kedah | Jitra | 11kV | Underground | 27-06-2026 11:17 | PPU LOJI AIR ARAU GIS 11K5 | PDB KLG BERAS PERING KJT01776 | PAT R22/1 RUMAH PAM SANGLANG :KJT19109 - PAT PIDA 15 SANGLANG :KJT19107 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 27-06-2026 11:50 | 27-06-2026 12:30 | 40 | 27-06-2026 16:20 | 28-06-2026 01:36 | 9 | 28-06-2026 01:47 | 14.5
Northern | K1 | TRIPPING-PLS-26-00052 | 2610/20260629/013 | Perlis | Perlis | 11kV | Underground | 29-06-2026 15:58 | PPU PADANG BESAR 11 | R PADANG BESAR 11 | PPU PADANG BESAR R PADANG BESAR CB11 - PDB TMN SINGGAHSANA :KAN02527 | Insulation Breakdown | Insulation Deterioration | Cable XLPE | CABLE | 29-06-2026 16:01 | 29-06-2026 16:57 | 56 | 29-06-2026 21:12 | 30-06-2026 04:07 | 6 | 30-06-2026 04:21 | 12.38 | 648M | 425M | 305M | 884M | 519M | 346M | 1.36 | 1.22 | 1.13
Northern | K1 | TRIPPING-KED-26-00508 | 0245/20260629/024 | Kedah | Kuala Nerang | 11kV | Underground | 29-06-2026 16:53 | PPU NAKA 4K5 | NAKA 33 4K5 | PAT KUBANG JULOK :KKN00369 - PAT KUBANG JULOK 2 :KKN00371 | Insulation Breakdown | Insulation Deterioration | Cable PILC | CABLE | 29-06-2026 16:58 | 29-06-2026 17:22 | 24 | 29-06-2026 22:04 | 30-06-2026 21:46 | 23 | 30-06-2026 22:10 | 29.28
Northern | K1 | TRIPPING-PLS-26-00053 | 2610/20260701/037 | Perlis | Perlis | 11kV | Underground | 01-07-2026 13:55 | PPU BUKIT KETERI 6K5 | PDB TMN BESERI JAYA KAN00176 | PAT PADANG MAJAI :KAN00358 - | Insulation Breakdown | Insulation Deterioration | Cable XLPE | SWITCHGEAR | 01-07-2026 14:02 | 01-07-2026 14:35 | 33 | 01-07-2026 17:45 | 01-07-2026 23:39 | 5 | 02-07-2026 00:59 | 11.07
Northern | K1 | TRIPPING-KED-26-00522 | 0242/20260703/018 | Kedah | Jitra | 11kV | Underground | 03-07-2026 23:34 | PPU DARULAMAN 11K5 | DARULAMAN 11K5 | PLB INFRASTRUKTUR FASA 2 :KJT00524 - | Open Circuit | Improper Installation | Cable XLPE | SWITCHGEAR | 03-07-2026 23:36 | 04-07-2026 00:10 | 34 | 04-07-2026 18:26, 06-07-2026 05:16 | 06-07-2026 04:15, 06-07-2026 21:00 | 33, 15 | 06-07-2026 21:14 | 69.67
Northern | K1 | TRIPPING-PLS-26-00054 | 2610/20260705/022 | Perlis | Perlis | 11kV | Underground | 05-07-2026 14:55 | PPU BUKIT KETERI 3K5 | PDB PANGGAS KAN00281 | PBT BILAL UDOH :KAN02440 - PBT SEMADONG 2 :KAN02486 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 05-07-2026 15:02 | 05-07-2026 15:40 | 38 | 07-07-2026 09:38 | 07-07-2026 22:31 | 12 | 07-07-2026 23:44 | 56.82
Northern | K1 | TRIPPING-PLS-26-00055 | 2610/20260705/043 | Perlis | Perlis | 11kV | Underground | 05-07-2026 15:09 | PMU KUALA PERLIS 7 | PDB PANGSAPURI KG.WAI KAN00647 | TMN WAI DAMAI :KAN03033 - PDB RPA SEBERANG RAMAI :KAN00643 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 05-07-2026 15:31 |  | 0 | 06-07-2026 16:22 | 07-07-2026 01:18 | 8 | 07-07-2026 01:31 | 34.37
Northern | K1 | TRIPPING-PLS-26-00056 | 2610/20260708/086 | Perlis | Perlis | 11kV | Underground | 08-07-2026 20:40 | PPU SHORUBBER 4 | SHORUBBER CB4 | PDB TMN DESA PULAI :KAN00712 - KOMPLEKS JPN PERLIS :KAN03361 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 08-07-2026 20:48 | 08-07-2026 21:15 | 27 | 09-07-2026 13:41 | 10-07-2026 01:40 | 11 | 10-07-2026 01:40 | 29 | 755M | 998M | 837M | 868M | 1.090G | 935M | 1.04 | 1 | 1.13
Northern | K1 | TRIPPING-KED-26-00534 | 0242/20260708/062 | Kedah | Jitra | 11kV | Underground | 08-07-2026 23:40 | PPU KODIANG KD5 | KODIANG KD5 | PPU KODIANG KD5 - PDB RUMAH PAM SG. PERING :KJT01274 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 09-07-2026 00:25 | 09-07-2026 00:34 | 9 | 09-07-2026 08:50 | 10-07-2026 01:31 | 16 | 10-07-2026 01:47 | 26.12
Northern | K1 | TRIPPING-PLS-26-00057 | 2610/20260712/050 | Perlis | Perlis | 11kV | Underground | 12-07-2026 22:43 | PMU KANGAR CB:16 | PDB TMN JALI KAN02326 | PDB LOT 42 TMN BUKIT KAYA :KAN00561 - MEDAN NIAGA KANGAR :KAN02715 | Insulation Breakdown | Mechanical damage due to old external wound | Cable XLPE | CABLE | 12-07-2026 22:46 | 12-07-2026 23:10 | 24 | 13-07-2026 09:56 | 14-07-2026 00:22 | 14 | 14-07-2026 00:36 | 25.88 | 93.3M | 63.4M | 78.9M
Northern | K1 | TRIPPING-PLS-26-00058 | 2610/20260717/013 | Perlis | Perlis | 11kV | Underground | 17-07-2026 09:42 | PPU UNIMAPS 2K5 | FELDA CHUPING NO.2 KAN02702 | PDB RUMAH PAM JKR :KAN00242 - PERLIS PLANTATION :KAN00238 |  |  |  | CABLE | 17-07-2026 09:59 | 17-07-2026 10:15 | 16 | 17-07-2026 17:51 | 18-07-2026 12:03 | 18 | 18-07-2026 12:16 | 26.57
Northern | K1 | TRIPPING-KED-26-00561 | 0242/20260717/038 | Kedah | Jitra | 11kV | Underground | 17-07-2026 12:06 | PMU TANJUNG PAUH TP20 | KLG DOUBLE SITE KJT01578 | PDB TMN SURIA 1 :KJT00015 - PDB TMN SURIA FASA 2 :KJT00016 |  |  |  | CABLE | 17-07-2026 12:11 | 17-07-2026 12:35 | 24 | 17-07-2026 14:42 | 17-07-2026 23:13 | 8 | 17-07-2026 23:40 | 11.57
Northern | K1 | TRIPPING-KED-26-00563 | 0242/20260717/182 | Kedah | Jitra | 11kV | Underground | 17-07-2026 21:28 | PMU TANJUNG PAUH TP15 | PDB TMN PASU KJT00468 | PDB TMN PASU :KJT00468 - PDB MADA JITRA :KJT00469 |  |  |  | CABLE | 17-07-2026 21:35 | 17-07-2026 22:20 | 45 | 18-07-2026 00:31 | 19-07-2026 08:38 | 32 | 19-07-2026 09:19 | 35.85
Northern | K1 | TRIPPING-PLS-26-00059 | 2610/20260720/019 | Perlis | Perlis | 11kV | Underground | 20-07-2026 09:49 | PMU CHUPING CB:10 | PDB UITM ARAU KAN00865 | PDB SMV ARAU :KAN00819 - TMN ENYUM INDAH :KAN02804 |  |  |  | CABLE | 20-07-2026 09:52 | 20-07-2026 10:10 | 18 | 20-07-2026 11:22 | 21-07-2026 00:43 | 13 | 21-07-2026 01:10 | 15.35 | 744M | 764M | 654M
Northern | K1 | TRIPPING-PLS-26-00060 | 2610/20260723/024 | Perlis | Perlis | 11kV | Underground | 23-07-2026 08:29 | PMU CHUPING CB:6 | PMU CHUPING CB:6 | PDB KOK KELANG 2 :KAN00250 - FELDA CHUPING NO.2 :KAN02698 |  |  |  | CABLE | 23-07-2026 08:38 | 23-07-2026 09:20 | 42 | 23-07-2026 14:40 | 24-07-2026 21:54 | 31 | 24-07-2026 22:13 | 37.73 | 163M | 247M | 171M
Northern | K1 | TRIPPING-KED-26-00582 | 0242/20260725/027 | Kedah | Jitra | 11kV | Underground | 25-07-2026 18:27 | PPU DARULAMAN 11K5 | PPU DARULAMAN 11K5 | PLB INFRASTRUKTUR FASA 2 :KJT00522 - SSD KLG ISO TECH :KJT00521 |  |  |  | CABLE | 25-07-2026 18:29 | 25-07-2026 19:40 | 71 | 25-07-2026 22:02 | 26-07-2026 21:51 | 23 | 26-07-2026 21:58 | 27.52 | 365M | 303M | 270M
Northern | K1 | TRIPPING-KED-26-00584 | 0242/20260726/027 | Kedah | Jitra | 11kV | Underground | 26-07-2026 15:42 | PPU LOJI AIR ARAU GIS 12K5 | PPU LOJI AIR ARAU GIS 12K5 | PDB KLG BERAS KOTA MANSYUR :KJT01300 - PLB RUMAH PAM KG. IMAM :KJT01299 |  |  |  | CABLE | 26-07-2026 15:47 | 26-07-2026 16:00 | 13 | 26-07-2026 22:07 | 27-07-2026 19:19 | 21 | 27-07-2026 19:27 | 27.75 | 266M | 280M | 252M
Northern | K1 | TRIPPING-KED-26-00585 | 0242/20260726/065 | Kedah | Jitra | 11kV | Underground | 26-07-2026 23:16 | PPU CHANGLOON CL4 | PDB QTRS SM HOSBA KJT01798 | PDB QTRS SM HOSBA :KJT01798 - PBT KG. KUBANG PASU :KJT00727 |  |  |  | CABLE | 26-07-2026 23:23 | 27-07-2026 00:16 | 53 | 27-07-2026 01:39 | 27-07-2026 23:25 | 21 | 27-07-2026 23:41 | 24.42 | 2.4G | 1.8G | 1.7G
Northern | K1 | TRIPPING-KED-26-00589 | 0242/20260728/018 | Kedah | Jitra | 11kV | Underground | 28-07-2026 16:31 | PPU DARULAMAN 10K5 | STN SUIS IKBN JITRA KJT18896 | PLB KLG SANKEI-VVIP :KJT00035 - PDB 17 UNIT R/KEDAI :KJT19279 |  |  |  | CABLE | 28-07-2026 16:58 | 28-07-2026 17:10 | 12 | 28-07-2026 20:55 | 29-07-2026 22:06 | 25 | 29-07-2026 22:15 | 29.73
Northern | K1 | TRIPPING-PLS-26-00061 | 2610/20260729/037 | Perlis | Perlis | 11kV | Underground | 29-07-2026 02:23 | PMU KANGAR CB:7 | TMN BUNGA PADI KAN00388 | TMN BUNGA PADI :KAN00388 - PDB LPP BINTONG :KAN00400 |  |  |  | CABLE | 29-07-2026 02:28 | 29-07-2026 02:40 | 12 | 29-07-2026 12:43 | 30-07-2026 21:59 | 33 | 31-07-2026 20:50 | 66.45 | 110M | 108M | 108M
Northern | K1 | TRIPPING-KED-26-00592 | 0242/20260729/006 | Kedah | Jitra | 11kV | Underground | 29-07-2026 04:40 | PPU JERLUN SJ6 | SMK PMTG BONGLAI KJT01518 | SMK PMTG.BONGLAI :KJT01518 - PLB PIDA 3 TUNJANG :KJT01519 |  |  |  | CABLE | 29-07-2026 04:57 | 29-07-2026 05:25 | 28 | 29-07-2026 13:48 | 29-07-2026 23:17 | 9 | 29-07-2026 23:29 | 18.82
Northern | K1 | TRIPPING-KED-26-00594 | 0242/20260729/037 | Kedah | Jitra | 11kV | Underground | 29-07-2026 08:56 | PMU TANJUNG PAUH TP17 | PMU TANJUNG PAUH TP17 | PMU TANJUNG PAUH TP17 - PDB PERMINTEX INDUSTRIES :KJT00495 |  |  |  | CABLE | 29-07-2026 08:59 | 29-07-2026 09:10 | 11 | 29-07-2026 10:55 | 30-07-2026 21:12 | 34 | 30-07-2026 21:48 | 36.87
Northern | K1 | TRIPPING-KED-26-00596 | 0245/20260730/011 | Kedah | Kuala Nerang | 11kV | Underground | 30-07-2026 19:24 | PPU KUALA NERANG 3K5 | PPU KUALA NERANG 3K5 | PBT KG. LUBOK IPOH :KKN00232 - PBT KG. MALAU-ALS :KKN00237 |  |  |  | CABLE | 30-07-2026 19:27 | 30-07-2026 20:00 | 33 | 30-07-2026 22:19 | 02-08-2026 03:56 | 53 | 02-08-2026 04:12 | 56.8 | 252M | 179M | 207M